| STATE OF GEORGIA GALVANIC (SACRIFICIAL ANODE) CATHODIC PROTECTION SYSTEM EVALUATION |
| --- |
| This form must be utilized to evaluate underground storage tank (UST) cathodic protection systems in the State of Georgia. Access to the soil directly over the cathodically protected structure that is being evaluated must be provided. A site drawing depicting the UST cathodic protection system and all reference electrode placements must be completed. |
| I. UST OWNER | II. UST FACILITY |
| NAME: | NAME: | ID # |
| ADDRESS: | ADDRESS: |
| CITY: | STATE: | CITY: | COUNTY: |
| III. CP TESTER | IV. CP TESTER’S QUALIFICATIONS |
| TESTER’S NAME: | NACE INTERNATIONAL CERTIFICATION NUMBER: |
| COMPANY NAME: | CERTIFICATION DATE: TYPE OF CERTIFICATION: |
| ADDRESS: | SOURCE OF CERTIFICATION: |
| CITY: | STATE: | OTHER (EXPLAIN) :_________________________________________________________ |
| V. REASON SURVEY WAS CONDUCTED (mark only one) |
| Routine - 3 year Routine – within 6 months of installation 60-day re-survey after fail Re-survey after repair/modification |
| Date next cathodic protection survey must be conducted by _____________________ (required within 6 months of installation/repair & every 3 years thereafter). |
| VI. CATHODIC PROTECTION TESTER’S EVALUATION (mark only one) |
| All protected structures at this facility pass the cathodic protection survey and it is judged that adequate cathodic protection has been provided to the UST system (indicate all criteria applicable by completion of Section VIII). |
| One or more protected structures at this facility fail the cathodic protection survey and it is judged that adequate cathodic protection has not been provided to the UST system (complete Section IX). |
| CP TESTER’S SIGNATURE: | DATE CP SURVEY PERFORMED: |
| VII. CORROSION EXPERT’S EVALUATION (mark only one) |
| The survey must be conducted and/or evaluated by a corrosion expert when: a) repairs to galvanized or uncoated steel piping are conducted or b) supplemental anodes are added to the tanks and/or piping without following an accepted industry code. |
| All protected structures at this facility pass the cathodic protection survey and it is judged that adequate cathodic protection has been provided to the UST system (indicate all criteria applicable by completion of Section VIII). |
| One or more protected structures at this facility fail the cathodic protection survey and it is judged that adequate cathodic protection has not been provided to the UST system (indicate what action is necessary by completion of Section IX). |
| CORROSION EXPERT’S NAME: | COMPANY NAME: |
| NACE INTERNATIONAL CERTIFICATION: | NACE INTERNATIONAL CERTIFICATION NUMBER: |
| CORROSION EXPERT’S SIGNATURE: | DATE: |
| VIII. CRITERIA APPLICABLE TO EVALUATION (mark all that apply) |
| Structure-to-soil potential more negative than –850 mV with respect to a Cu/CuSO4 reference electrode with the protective current applied (This criterion is applicable to any galvanically protected structure). |
| IX. ACTION REQUIRED AS A RESULT OF THIS EVALUATION (mark only one) |
| NONE Cathodic protection is adequate. No further action is necessary at this time. Test again by no later than (see Section V). REPAIR & RETEST Cathodic protection is not adequate. Repair/modification is necessary as soon as practical but within the next 60 days. |
| EPD, UST MANAGEMENT PROGRAM 4244 INTERNATIONAL PKWY, ATLANTA, GA 30354 PHONE 404) 362-2687 FAX (8404) 362-2654 www.dnr.state.ga.us/dnr/environ |

| X. DESCRIPTION OF UST SYSTEM |
| --- |
| TANK # | PRODUCT | CAPACITY | TANKS | PIPING | FLEX CONNECTORS |
| 1 |  |  |  |  |  |
| 2 |  |  |  |  |  |
| 3 |  |  |  |  |  |
| 4 |  |  |  |  |  |
| 5 |  |  |  |  |  |
| 6 |  |  |  |  |  |
| 7 |  |  |  |  |  |
| 8 |  |  |  |  |  |
| 9 |  |  |  |  |  |
| 10 |  |  |  |  |  |
| XI. DESCRIPTION OF CATHODIC PROTECTION SYSTEM REPAIRS AND/OR MODIFICATION |
| Complete if any repairs or modifications to the cathodic protection system are made or are necessary. Certain repairs/modifications as explained in the text of the EPD cathodic protection guidance document are required to be designed and/or evaluated by a corrosion expert (completion of Section VII required). |
| Supplemental anodes for a sti-P3® tank (attach corrosion expert’s design or documention industry standard was followed). |
| Supplemental anodes for metallic pipe (attach corrosion expert’s design or documention industry standard was followed). |
| Galvanically protected tanks/piping not electrically isolated (explain in “Remarks/Other” below). |
| Remarks/Other: ____________________________________________________________________________________________________________ _________________________________________________________________________________________________________________________ _________________________________________________________________________________________________________________________ |
| XII. UST FACILITY SITE DRAWING |
| Attach detailed drawing or use the space provided to draw a sketch of the UST and cathodic protection systems. Sufficient detail must be given in order to clearly indicate where the reference electrode was placed for each structure-to-soil potential that is recorded on the survey forms. Any pertinent data must also be included. At a minimum you should indicate the following: All tanks, piping and dispensers; All buildings and streets; All anodes and wires; Location of CP test stations; Each reference electrode placement must be indicated by a code (1,2, T-1,) corresponding with the appropriate line number in Section XIV of this form. AN EVALUATION OF THE CATHODIC PROTECTION SYSTEM IS NOT COMPLETE WITHOUT AN ACCEPTABLE SITE DRAWING. |
| EPD, UST MANAGEMAENT PROGRAM 4244 INTERNATIONAL PKWY, ATLANTA, GA 30354 PHONE (404) 362-2687 FAX (404) 362-2654 www.dnr.state.ga.us/dnr/environ |
| XIII. GALVANIC (SACRIFICIAL ANODE) CATHODIC PROTECTION SYSTEM CONTINUITY SURVEY |
| This section may be utilized to conduct measurements of continuity on underground storage tank systems that are protected by cathodic protection systems. When conducting a fixed cell - moving ground survey, the reference electrode must be placed in the soil at a remote location and left undisturbed. For galvanic systems, the structure that is to be protected must be isolated from any other metallic structure in order to pass the continuity survey. |
| FACILITY NAME: | NOTE: The survey is not complete unless all applicable parts of Sections I-XIV are also completed |
| DESCRIBE LOCATION OF “FIXED REMOTE” REFERENCE ELECTRODE PLACEMENT: |
| Contact Points | Potential (mV) | Comments | ISOLATED/ 6 CONTINUOUS/ INCONCLUSIVE |
| Tank 1 |  |  |  |
| A. Tank Bottom/Test Lead |  |  |  |
| B. Fill Pipe Riser |  |  |  |
| C. Submersible Pump |  |  |  |
| D. Tank Monitor |  |  |  |
| E. Piping at sub pump |  |  |  |
| F. Vent Line |  |  |  |
| Tank 2 |  |  |  |
| A. Tank Bottom/Test Lead |  |  |  |
| B. Fill Pipe Riser |  |  |  |
| C. Submersible Pump |  |  |  |
| D. Tank Monitor |  |  |  |
| E. Piping at sub pump |  |  |  |
| F. Vent Line |  |  |  |
| Tank 3 |  |  |  |
| A. Tank Bottom/Test Lead |  |  |  |
| B. Fill Pipe Riser |  |  |  |
| C. Submersible Pump |  |  |  |
| D. Tank Monitor |  |  |  |
| E. Piping at sub pump |  |  |  |
| F. Vent Line |  |  |  |
| Dispensers |  |  |  |
| No. 1 |  | No. 5 |  |
| No. 2 |  | No. 6 |  |
| No. 3 |  | No. 7 |  |
| No. 4 |  | No. 8 |  |
| COMMENTS: |
| EPD, UST MANAGEMENT PROGRAM 4244 INTERNATIONAL PKWY, ATLANTA, GA 30354 PHONE (404) 362-2687 FAX (404) 362-2654 www.dnr.state.ga.us/dnr/environ |
| XIV. GALVANIC (SACRIFICIAL ANODE) CATHODIC PROTECTION SYSTEM SURVEY |
| This section may be utilized to conduct a survey of a galvanic cathodic protection system by obtaining structure-to-soil potential measurements. The reference electrode must be placed in the soil directly over the tested structure (local). |
| FACILITY NAME: | NOTE: The survey is not complete unless all applicable parts of sections I – XIV are also completed |
| DESCRIBE LOCATION OF REMOTE REFERENCE ELECTRODE PLACEMENT: |
| Reference Cell Location | Potential (mV) | Comments | PASS/FAIL/ INCONCLUSIVE |
| Tank 1 |  |  |  |
| A. Tank Bottom/Test Lead |  |  |  |
| B. Fill Piper Riser |  |  |  |
| C. Submersible Pump |  |  |  |
| D. Tank Monitor |  |  |  |
| E. Piping at sub pump |  |  |  |
| F. Vent Line |  |  |  |
| Tank 2 |  |  |  |
| A. Tank Bottom/Test Lead |  |  |  |
| B. Fill Piper Riser |  |  |  |
| C. Submersible Pump |  |  |  |
| D. Tank Monitor |  |  |  |
| E. Piping at sub pump |  |  |  |
| F. Vent Line |  |  |  |
| Tank 3 |  |  |  |
| A. Tank Bottom/Test Lead |  |  |  |
| B. Fill Piper Riser |  |  |  |
| C. Submersible Pump |  |  |  |
| D. Tank Monitor |  |  |  |
| E. Piping at sub pump |  |  |  |
| F. Vent Line |  |  |  |
| Dispensers |  |  |  |
| No. 1 |  |  |  |
| No. 2 |  |  |  |
| No. 3 |  |  |  |
| No. 4 |  |  |  |
| No. 5 |  |  |  |
| COMMENTS: |
| Designate numerically or by code on the site drawing each “local” reference electrode placement (e.g. 1,2,3… T-1, T-2, P-1, P-2…etc.). |
| Describe the exact location where reference electrode is placed for each “local” measurement (e.g. soil @ plus tank STP; soil @ dispenser 5/6; etc.) |
| Record the structure-to-soil potential measured with the reference electrode placed “local” in millivolts (e.g. –865 mV, -920 mV, etc.). |
| Indicate whether the tested structure passed or failed the –850 mV “on” criterion based on your interpretation of the test data. |
| EPD, UST MANAGEMENT PROGRAM 4244 INTERNATIONAL PKWY, ATLANTA, GA 30354 PHONE (404) 362-2687 FAX (404) 362-2654 www.dnr.state.ga.us/dnr/environ |
| STATE OF GEORGIA IMPRESSED CURRENT CATHODIC PROTECTION SYSTEM EVALUATION |
| This form must be utilized to evaluate underground storage tank (UST) cathodic protection systems in Georgia. Access to the soil directly over the cathodically protected structure that is being evaluated must be provided. A site drawing depicting the UST cathodic protection system and all reference electrode placements must be completed. |
| I. UST OWNER | II. UST FACILITY |
| NAME: | NAME: | ID # |
| ADDRESS: | ADDRESS: |
| CITY: | STATE: | CITY: | COUNTY: |
| III. CP TESTER | IV. CP TESTER’S QUALIFICATIONS |
| TESTER’S NAME: | NACE INTERNATIONAL CERTIFICATION NUMBER: |
| COMPANY NAME: | CERTIFICATION DATE: TYPE OF CERTIFICATION: |
| ADDRESS: | SOURCE OF CERTIFICATION: |
| CITY: | STATE: | OTHER (EXPLAIN) : _________________________________________________________ |
| V. REASON SURVEY WAS CONDUCTED (mark only one) |
| Routine - 3 year Routine – within 6 months of installation 60-day re-survey after fail Re-survey after repair/modification |
| Date next cathodic protection survey must be conducted ______________________ (required within 6 months of installation/repair & every 3 years thereafter). |
| VI. CATHODIC PROTECTION TESTER’S EVALUATION (mark only one) |
| All protected structures at this facility pass the cathodic protection survey and it is judged that adequate cathodic protection has been provided to the UST system (indicate all criteria applicable by completion of Section VIII). |
| One or more protected structures at this facility fail the cathodic protection survey and it is judged that adequate cathodic protection has not been provided to the UST system (complete Section IX). |
| The cathodic protection survey of an impressed current system must be evaluated by a corrosion expert because one or more of the conditions listed in Section 7.1.5 of the EPD cathodic protection guidance document are applicable (complete Section VII). |
| CP TESTER’S SIGNATURE: | DATE CP SURVEY PERFORMED: |
| VII. CORROSION EXPERT’S EVALUATION (mark only one) |
| The survey must be conducted and/or evaluated by a corrosion expert when: a) supplemental anodes or other changes in the construction of the impressed current system are made; b) stray current may be affecting buried metallic structures or c) an inconclusive result was indicated in Section VI. |
| All protected structures at this facility pass the cathodic protection survey and it is judged that adequate cathodic protection has been provided to the UST system (indicate all criteria applicable by completion of Section VIII). |
| One or more protected structures at this facility fail the cathodic protection survey and it is judged that adequate cathodic protection has not been provided to the UST system (indicate what action is necessary by completion of Section IX). |
| CORROSION EXPERT’S NAME: | COMPANY NAME: |
| NACE INTERNATIONAL CERTIFICATION: | NACE INTERNATIONAL CERTIFICATION NUMBER: |
| CORROSION EXPERT’S SIGNATURE: | DATE: |
| VIII. CRITERIA APPLICABLE TO EVALUATION (mark all that apply) |
| Structure-to-soil potential more negative than –850 mV with respect to a Cu/CuSO4 reference electrode with protective current temporarily interrupted (instant-off). Structure(s) exhibit at least 100 mV of cathodic polarization. |
| IX. ACTION REQUIRED AS A RESULT OF THIS EVALUATION (mark only one) |
| NONE Cathodic protection is adequate. No further action is necessary at this time. Test again by no later than (see Section V). REPAIR & RETEST Cathodic protection is not adequate. Repair/modification is necessary as soon as practical but within the next 60 days. |
| EPD, UST MANAGEMENT PROGRAM 4244 INTERNATIONAL PKWY, ATLANTA, GA 30354 PHONE (404) 362-2687 FAX (404) 362-2654 www.dnr.state.ga.us/dnr/environ |
| X. DESCRIPTION OF UST SYSTEM |
| TANK # | PRODUCT | CAPACITY | TANK MATERIAL | PIPING MATERIAL | FLEX CONNECTORS |
| 1 |  |  |  |  |  |
| 2 |  |  |  |  |  |
| 3 |  |  |  |  |  |
| 4 |  |  |  |  |  |
| 5 |  |  |  |  |  |
| 6 |  |  |  |  |  |
| 7 |  |  |  |  |  |
| 8 |  |  |  |  |  |
| 9 |  |  |  |  |  |
| 10 |  |  |  |  |  |
| XI. IMPRESSED CURRENT RECTIFIER DATA (complete all applicable) |
| In order to conduct an effective evaluation of the cathodic protection system, a complete evaluation of rectifier operation is necessary. |
| RECTIFIER MANUFACTURER: | RATED DC OUTPUT: | ____________ VOLTS ____________ AMPS |
| RECTIFIER MODEL: | RECTIFIER SERIAL NUMBER: |
| RECTIFIER OUTPUT AS INITIALLY DESIGNED OR LASTLY RECOMMENDED (if available): __________ VOLTS __________ AMPS |
| EVENT | DATE | COARSE | FINE | VOLTS | AMPS | HOUR METER | COMMENTS |
| “AS FOUND” |  |  |  |  |  |  |  |
| “AS LEFT” |  |  |  |  |  |  |  |
| XII. IMPRESSED CURRENT POSITIVE & NEGATIVE CIRCUIT MEASUREMENTS (output amperage) |
| Complete if the system is designed to allow such measurements (i.e. individual lead wires for each anode are installed and measurement shunts are present). |
| CIRCUIT | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | TOTAL AMPS |
| ANODE (+) |  |  |  |  |  |  |  |  |  |  |  |
| TANK (-) |  |  |  |  |  |  |  |  |  |  |  |
| XIII. DESCRIPTION OF CATHODIC PROTECTION SYSTEM REPAIRS AND/OR MODIFICATION |
| Complete if any repairs or modifications to the cathodic protection system are made OR are necessary. Certain repairs/modifications as explained in the text of the EPD cathodic protection guidance document are required to be designed and/or evaluated by a corrosion expert (completion of Section VII required). |
| Additional anodes for an impressed current system (attach corrosion expert’s design). |
| Repairs or replacement of rectifer (explain in “Remarks/Other” below). |
| Anode header cables repaired and/or replaced(explain in “Remarks/Other” below). |
| Impressed current protected tanks/piping not electrically continuous (explain in “Remarks/Other” below). |
| Remarks/Other: _____________________________________________________________________________________________________ _________________________________________________________________________________________________________________________ _________________________________________________________________________________________________________________________ |
| XIV. UST FACILITY SITE DRAWING |
| Attach detailed drawing of the UST and cathodic protection systems. Sufficient detail must be given in order to clearly indicate where the reference electrode was placed for each structure-to-soil potential that is recorded on the survey forms. Any pertinent data must also be included. At a minimum you should indicate the following: All tanks, piping and dispensers; All buildings and streets; All anodes and wires; Location of CP test stations; Each reference electrode placement must be indicated by a code (1,2,3 R-1, R-2, R-3…etc.) corresponding with the appropriate line number in Section XVI of this form. AN EVALUATION OF THE CATHODIC PROTECTION SYSTEM IS NOT COMPLETE WITHOUT AN ACCEPTABLE SITE DRAWING. |
| EPD, UST MANAGEMENT PROGRAM 4244 INTERNATIONAL PKWY, ATLANTA, GA 30354 PHONE (404) 362-2687 FAX (404) 362-2654 www.dnr.state.ga.us/dnr/environ |
| XV. IMPRESSED CURRENT CATHODIC PROTECTION SYSTEM CONTINUITY SURVEY |
| This section may be utilized to conduct measurements of continuity on underground storage tank systems that are protected by cathodic protection systems. When conducting a fixed cell - moving ground survey, the reference electrode must be placed in the soil at a remote location and left undisturbed. For impressed current systems, the protected structure must be continuous with all other protected structures in order to pass the continuity survey. |
| FACILITY NAME: | NOTE: The survey is not complete unless all applicable parts of sections I-XIV are also completed |
| DESCRIBE LOCATION OF “FIXED REMOTE” REFERENCE ELECTRODE PLACEMENT: |
| CONTACT POINT | STRUCTURE “A” 3 FIXED REMOTE INSTANT OFF VOLTAGE | STRUCTURE “B” 4 FIXED REMOTE INSTANT OFF VOLTAGE | ISOLATED/ 6 CONTINUOUS/ INCONCLUSIVE |
| TANK 1 |  |  |  |
| A. Tank Bottom/Test Lead |  |  |  |
| B. Fill Pipe Riser |  |  |  |
| C. Submersible Pump |  |  |  |
| D. Tank Monitor |  |  |  |
| E. Piping at sub pump |  |  |  |
| F. Vent Line |  |  |  |
| TANK 2 |  |  |  |
| A. Tank Bottom/Test Lead |  |  |  |
| B. Fill Pipe Riser |  |  |  |
| C. Submersible Pump |  |  |  |
| D. Tank Monitor |  |  |  |
| E. Piping at sub pump |  |  |  |
| F. Vent Line |  |  |  |
| TANK 3 |  |  |  |
| A. Tank Bottom/Test Lead |  |  |  |
| B. Fill Pipe Riser |  |  |  |
| C. Submersible Pump |  |  |  |
| D. Tank Monitor |  |  |  |
| E. Piping at sub pump |  |  |  |
| F. Vent Line |  |  |  |
| Dispensers |  |  |  |
| No. 1 |  |  |  |
| No. 2 |  |  |  |
| No. 3 |  |  |  |
| Comments: |
| EPD, UST MANAGEMENT PROGRAM 4244 INTERNATIONAL PKWY, ATLANTA, GA 30354 PHONE (404) 362-2687 FAX (404) 362-2654 www.dnr.state.ga.us/dnr/environ |
| XVI. IMPRESSED CURRENT CATHODIC PROTECTION SYSTEM SURVEY |
| This section may be utilized to conduct a survey of an impressed current cathodic protection system by obtaining structure-to-soil potential measurements. The reference electrode must be placed in the soil directly above the structure that is being tested and as far away from any active anode as practical to obtain a valid structure-to-soil potential (refer to the EPD cathodic protection evaluation guidance document for detailed discussion of electrode placement). Both on and instant off potentials must be measured for each structure that is intended to be under cathodic protection. The instant off potential must be -850 mV or more negative or the 100 mV polarization criterion must be satisfied in order to pass. |
| FACILITY NAME: | NOTE: This survey is not complete unless all applicable parts of sections I – XIV are also completed |
| LOCATION CODE | Location of Cell Contact to Tank | ON VOLTAGE | INSTANT OFF VOLTAGE | 100 mV POLARIZATION | PASS/ FAIL 9 |
|  |  |  |  | Ending Voltage | Voltage Change |  |
|  | Tank 1 |  |  |  |  |  |
|  | A. Sub Pump Pit |  |  |  |  |  |
|  | B. Tank Monitor Pit |  |  |  |  |  |
|  | C. Vapor Riser Pit |  |  |  |  |  |
|  | Tank 2 |  |  |  |  |  |
|  | A. Sub Pump Pit |  |  |  |  |  |
|  | B. Tank Monitor Pit |  |  |  |  |  |
|  | C. Vapor Riser Pit |  |  |  |  |  |
|  | Tank 3 |  |  |  |  |  |
|  | A. Sub Pump Pit |  |  |  |  |  |
|  | B. Tank Monitor Pit |  |  |  |  |  |
|  | C. Vapor Riser Pit |  |  |  |  |  |
|  | Tank 4 |  |  |  |  |  |
|  | A. Sub Pump Pit |  |  |  |  |  |
|  | B. Tank Monitor Pit |  |  |  |  |  |
|  | C. Vapor Riser Pit |  |  |  |  |  |
|  | Dispensers |  |  |  |  |  |
|  | No. 1 |  |  |  |  |  |
|  | No. 2 |  |  |  |  |  |
|  | No. 3 |  |  |  |  |  |
|  | No. 4 |  |  |  |  |  |
| COMMENTS: |
| Designate numerically or by code on the site drawing each local reference electrode placement (e.g. 1,2,3… T-1, T-2, P-1, P-2…etc.). |
| Describe the exact location where the reference electrode is placed for each measurement (e.g. soil @ regular tank STP manway; soil @ dispenser 2, etc.) |
| {Applies to all tests} Record the structure-to-soil potential (voltage) observed with the current applied (e.g. –1070 mV). |
| {Applies to all tests} Record the structure to soil potential (voltage) observed when the current is interrupted (e.g. 680 mV). |
| {Applies to 100 mV polarization test only} Record the voltage observed at the end of the test period (e.g. 575 mV). |
| {Applies to 100 mV polarization test only} Subtract the final voltage from the instant off voltage (e.g. 680 mV – 575 mV = 105 mV). |
| Indicate if the tested structure passed or failed one of the two acceptable criteria (850 instant off or 100 mV polarization) based on your interpretation of data. |
| EPD, UST MANAGEMENT PROGRAM 4244 INTERNATIONAL PKWY, ATLANTA, GA 30354 PHONE (404) 362-2687 FAX (404) 362-2654 www.dnr.state.ga.us/dnr/environ |

| STATE OF GEORGIA IMPRESSED CURRENT CATHODIC PROTECTION SYSTEM 60-DAY RECORD OF RECTIFER OPERATION |
| --- |
| This form may be utilized to document that the cathodic protection system rectifier is checked for operation at least once every 60 days. Checked for operation is taken to mean that it was confirmed the rectifier was receiving power and is “turned-on”. If your rectifier is so equipped, you should also record the output voltage, amperage and the number of hours indicated on the meter. Any significant variance should be reported to your corrosion professional so that any repairs and/or adjustments necessary can be made. |
| UST OWNER | UST FACILITY |
| NAME: | NAME: | ID # |
| ADDRESS: | ADDRESS: |
| CITY: | STATE: | CITY: | COUNTY: |
| IMPRESSED CURRENT RECTIFIER DATA |
| Rectifier Manufacturer: | Rated DC Output: ____________ VOLTS ___________AMPS |
| Rectifier Model: | Rectifier Serial Number: |
| What is the ‘as designed’ or lastly recommended rectifier output? ____________ VOLTS ___________AMPS |
| 60-DAY LOG OF RECTIFIER OPERATION |
| DATE INSPECTED | RECTIFIER TURNED ON? | COARSE | FINE | VOLTS | AMPS | HOUR METER | INSPECTOR INITIALS | COMMENTS |
| EPD, UST MANAGEMENT PROGRAM 4244 INTENATIONAL PKWY, ATLANTA, GA 30354 PHONE 404) 362-2687 FAX (404) 362-2654 www.dnr.state.ga.us/dnr/environ |

# Text boxes

###### TAP SETTINGS

DC OUTPUT

TAP SETTINGS

FAIL

PASS

FAIL

PASS

###### DC OUTPUT

100 mV POLARIZATION

850 OFF

FAIL

PASS

INCONCLUSIVE

FAIL

PASS

850 ON