## 2018 Final
Name of City / Utility: 2018 Validated Water Audit | WSID Number | Service County | Population Served | Volume From Own Sources (Million gallons / Year) | Water Imported (Million gallons / Year) | Water Exported (Million gallons / Year) | Water Supplied (Million gallons / Year) | Billed Metered (Million gallons / Year) | Billed Unmetered (Million gallons / Year) | Unbilled Metered (Million gallons / Year) | Unbilled Unmetered (Million gallons / Year) | Authorized Consumption (Million gallons / Year) | Water Losses (Million gallons / Year) | Apparent Losses (Million gallons / Year) | Real Losses (Million gallons / Year) | Non-Revenue Water (Million gallons / Year) | Length of Mains (miles) | Number of Active and Inactive Service Connections | Average Operating Pressure (psi) | Total Annual Cost of Operating Water System | Customer Retail Unit Cost ( $ / 1000 gallons) | Variable Production Cost | Unavoidable Annual Real Losses (UARL) (Million gallons) | Annual Cost of Apparent Losses | Annual Cost of Real Losses | Value Applied to Real Losses (VPC / CRUC) | Non-Revenue Water as % by Volume of Water Supplied | Non-Revenue Water as % by Cost of Operating System | Apparent Losses per service connection per day | Real Losses per service connection per day | Real Losses per length of main per day | Current Annual Real Losses (CARL) (Million Gallons) | Infrastructure Leakage Index (ILI) | Water Audit Data Validity Score | Priority Area #1 | Priority Area #2 | Priority Area #3
Adairsville | GA0150000 | Bartow | 3600 | 537.23 | 0 | 92.11 | 444.9077 | 258.5535 | 0.132 | 0.17062 | 5.5613 | 264.4175 | 180.4902 | 9.7604 | 170.7298 | 186.2222 | 87.9 | 2810 | 85 | 1747745.5 | 2.61 | 411.34 | 27.8306 | 25474.72 | 70227.98 | VPC | 41.86% | 5.611% | 9.5163 | N/A | 5321.4196 | 170.7298 | 6.1346 | 65.1577 | Volume from own sources | Unbilled metered | Customer metering inaccuracies
Adel | GA0750000 | Cook | 5252 | 300.101 | 0 | 0 | 300.101 | 203.575 | Note 1 | 2.04 | 3.7513 | 209.3663 | 90.7347 | 3.3361 | 87.3986 | 96.526 | 74.2 | 2711 | 54 | 859125 | 2.54 | 3.49 | 15.9271 | 8473.72 | 221992.52 | CRUC | 32.16% | 28.54% | 3.3715 | 88.3247 | N/A | 87.3986 | 5.4874 | 63.3824 | Volume from own sources | Unbilled metered | Variable production cost (applied to Real Losses)
Alamo | GA3090000 | Wheeler | 3653 | 137.325 | 0 | 0 | 143.0469 | 123.315 | Note 1 | Note 1 | 1.7881 | 125.1031 | 17.9438 | 5.804 | 12.1398 | 19.7319 | 25 | 358 | 45 | 63527.01 | 3.84 | 204.27 | Note 3 | 22287.47 | 2479.79 | VPC | 13.79% | 39.56% | 44.4175 | N/A | 1330.3846 | 12.1398 | Note 3 | 46.6641 | Volume from own sources | Customer metering inaccuracies | Billed metered
Albany | GA0950000 | Dougherty | 87029 | 3991.052 | 0 | 0 | 4051.0069 | 3645.5 | 0 | 59.15 | 61.9 | 3766.55 | 284.4569 | 94.8464 | 189.6105 | 405.5069 | 675 | 38939 | 55 | 8961901 | 5.31 | 233.27 | 190.5639 | 503634.22 | 44230.45 | VPC | 10.01% | 6.428% | 6.6733 | 13.3409 | N/A | 189.6105 | 0.995 | 66.4899 | Volume from own sources | Customer metering inaccuracies | Billed metered
Alma | GA0050000 | Bacon | 4700 | 189.318 | 0 | 0 | 192.9847 | 153.574 | 0 | 11.607 | 14.05 | 179.231 | 13.7537 | 3.3818 | 10.3719 | 39.4107 | 48 | 1951 | 60 | 322786 | 3.29 | 190.57 | 12.096 | 11126.27 | 1976.57 | VPC | 20.42% | 5.574% | 4.749 | 14.5649 | N/A | 10.3719 | 0.85746 | 64.9451 | Variable production cost (applied to Real Losses) | Unbilled metered | Total annual cost of operating water system
Americus | GA2610000 | Sumter | 16255 | 854.519 | 0 | 0 | 852.992 | 617.46 | 2.247 | 0 | 10.6624 | 630.3694 | 222.6226 | 16.2774 | 206.3452 | 233.285 | 176.4 | 7253 | 66.25 | 4272808 | 2.92 | 210.67 | 49.3847 | 47548.24 | 43470.07 | VPC | 27.35% | 2.183% | 6.1486 | 77.9442 | N/A | 206.3452 | 4.1783 | 59.188 | Volume from own sources | Customer metering inaccuracies | Billed metered
Ashburn | GA2870000 | Turner | 4178 | 225.047 | 0 | 0 | 281.3087 | 146.954 | 0 | 4.269 | 3.5164 | 154.7394 | 126.5694 | 14.2205 | 112.3489 | 134.3547 | 45 | 2600 | 47.5 | 702444 | 2.66 | 248.73 | 10.9824 | 37826.48 | 27944.54 | VPC | 47.76% | 9.639% | 14.9847 | 118.3866 | N/A | 112.3489 | 10.2299 | 51.0245 | Volume from own sources | Master meter error adjustment | Customer metering inaccuracies
Athens-Clarke County | GA0590000 | Clarke | 120266 | 4553.4 | 0 | 0 | 4553.4 | 3995.2399 | Note 1 | 50.8694 | 61.9989 | 4108.1082 | 445.2918 | 62.2414 | 383.0504 | 558.1601 | 804.5 | 43053 | 89.5 | 8222291.95 | 7.34 | 304.96 | 353.1453 | 457073.96 | 116815.06 | VPC | 12.26% | 7.398% | 3.9608 | 24.3758 | N/A | 383.0504 | 1.0847 | 81.7157 | Billed metered | Customer metering inaccuracies | Volume from own sources
Atlanta | GA1210001 | Fulton | 650000 | 31261.85 | 4482.32 | 1095.24 | 34709.6023 | 24817.24 | 1.37 | 0 | 433.87 | 25252.48 | 9457.1223 | 1001.1343 | 8455.988 | 9890.9923 | 2835 | 202481 | 103 | 150204707.63 | 6.38 | 327.84 | 1718.4487 | 6387236.74 | 2772211.1 | VPC | 28.5% | 6.193% | 13.5461 | 114.4161 | N/A | 8455.988 | 4.9207 | 73.8577 | Customer metering inaccuracies | Variable production cost (applied to Real Losses) | Billed metered
Auburn | GA0130000 | Barrow | 6904 | 0 | 162.7251 | 0 | 162.3193 | 158.9197 | 0 | 0 | 2.029 | 160.9486 | 1.3706 | 1.2014 | 0.16922 | 3.3996 | 75 | 2842 | 49.2 | 1516863 | 7.53 | 533.7 | 14.942 | 9046.48 | 90.31 | VPC | 2.094% | 0.6737% | 1.1582 | 0.16313 | N/A | 0.16922 | 0.011325 | 81.6048 | Water imported | Unauthorized consumption | Systematic data handling errors
Augusta | GA2450000 | Richmond | 204000 | 12966.56 | 0 | 0 | 12608.4792 | 10877.575 | Note 1 | 337.356 | 72.77 | 11287.701 | 1320.7782 | 341.9793 | 978.7989 | 1730.9042 | 1301.19 | 65952 | 81 | 50609506.23 | 5.56 | 232.31 | 500.6016 | 1901405.14 | 227383.39 | VPC | 13.73% | 4.395% | 14.2062 | 40.6605 | N/A | 978.7989 | 1.9552 | 67.612 | Volume from own sources | Customer metering inaccuracies | Billed metered
Austell | GA0670001 | Cobb | 7774 | 0 | 328.222 | 0 | 329.8714 | 266.1274 | 0 | 3.019 | 4.1234 | 273.2698 | 56.6016 | 6.9828 | 49.6188 | 63.744 | 62.52 | 3511 | 128 | 1878265.03 | 6.96 | 1712.55 | 40.4073 | 48600.15 | 84974.65 | VPC | 19.32% | 7.763% | 5.4488 | 38.7188 | N/A | 49.6188 | 1.228 | 77.9434 | Water imported | Customer metering inaccuracies | Billed metered
Bainbridge | GA0870001 | Decatur | 13302 | 952.933 | 0 | 0 | 952.933 | 629.922 | 0 | 4 | 11.9117 | 645.8337 | 307.0993 | 10.3604 | 296.7389 | 323.011 | 161 | 5550 | 52 | 195000 | 2.05 | 150 | 32.3326 | 21238.8 | 608314.84 | CRUC | 33.9% | 339.6% | 5.1143 | 146.4835 | N/A | 296.7389 | 9.1777 | 50.8922 | Volume from own sources | Billed metered | Variable production cost (applied to Real Losses)
Baldwin | GA1370001 | Habersham | 4160 | 678.979 | 0 | 478.89 | 194.4199 | 116.021 | 0.012 | 2.73 | 2.4302 | 121.1932 | 73.2267 | 9.1675 | 64.0592 | 78.3869 | 38.7 | 1700 | 103 | 1857301 | 3.25 | 761 | Note 3 | 29794.38 | 48749.03 | VPC | 40.32% | 4.44% | 14.7744 | 103.238 | N/A | 64.0592 | Note 3 | 73.985 | Water exported | Customer retail unit cost (applied to Apparent Losses) | Variable production cost (applied to Real Losses)
Baldwin County Water & Sewer | GA0090000 | Baldwin | 22279 | 0 | 721.689 | 0.333 | 728.6424 | 449.624 | 0 | 53.256 | 9.108 | 511.988 | 216.6544 | 15.84 | 200.8144 | 279.0184 | 420 | 11416 | 60 | 4219109.88 | 4.5 | 558.31 | 87.2627 | 71280.11 | 112116.67 | VPC | 38.29% | 5.172% | 3.8014 | N/A | 1309.9437 | 200.8144 | 2.3013 | 66.0998 | Water imported | Billed metered | Customer metering inaccuracies
Banks County | GA0110026 | Banks | 6453 | 246.37 | 19.106 | 44.01 | 226.4393 | 177.753 | 0 | 26.972 | 2.8305 | 207.5555 | 18.8838 | 2.0392 | 16.8446 | 48.6863 | 320 | 2900 | 99.5 | 1483865.18 | 6.65 | 728.66 | 78.671 | 13561.01 | 12273.98 | VPC | 21.5% | 3.205% | 1.9265 | N/A | 144.2174 | 16.8446 | 0.21411 | 62.0853 | Volume from own sources | Customer metering inaccuracies | Billed metered
Barnesville | GA1710000 | Lamar | 6755 | 641.91 | 2.967 | 0 | 638.4921 | 351.333 | 0.39063 | 3.889 | 7.9812 | 363.5938 | 274.8983 | 9.724 | 265.1743 | 286.7684 | 81 | 4178 | 90 | 2043713.8 | 5.8 | 773.36 | 34.9823 | 56399.15 | 205075.2 | VPC | 44.91% | 13.24% | 6.3765 | 173.8882 | N/A | 265.1743 | 7.5802 | 72.7114 | Volume from own sources | Customer metering inaccuracies | Billed metered
Barrow County Water | GA0130031 & GA0130034 | Barrow | 14043 | 0 | 779 | 298 | 443.0361 | 344.177 | 0.076 | 0.022 | 5.538 | 349.813 | 93.2231 | 16.3097 | 76.9135 | 98.7831 | 155 | 5876 | 101.6 | 4883582 | 7.19 | 474 | 63.7826 | 117266.44 | 36456.98 | VPC | 22.3% | 3.202% | 7.6045 | 35.8614 | N/A | 76.9135 | 1.2059 | 61.3159 | Water imported | Unbilled metered | Customer metering inaccuracies
Bartow County | GA0150001 | Bartow | 50162 | 131.306 | 2250.1468 | 19.251 | 2379.0504 | 1747.285 | 2.45 | 0 | 29.7381 | 1779.4731 | 599.5772 | 36.9242 | 562.653 | 629.3154 | 936 | 23707 | 120 | 14829208.01 | 7.32 | 2764.35 | 377.5477 | 270254.32 | 4118145.85 | CRUC | 26.45% | 31.06% | 4.2672 | N/A | 1646.9178 | 562.653 | 1.4903 | 63.7643 | Water imported | Billed metered | Customer metering inaccuracies
Baxley | GA0010000 | Appling | 4741 | 248.801 | 0 | 0 | 240.5036 | 188.31 | 0 | 29.425 | 3.0063 | 220.7413 | 19.7623 | 3.2714 | 16.491 | 52.1936 | 108.4 | 3806 | 58 | 565035.31 | 3.71 | 462.44 | 24.501 | 12136.81 | 7626.08 | VPC | 21.7% | 6.152% | 2.3549 | 11.8709 | N/A | 16.491 | 0.67307 | 69.0392 | Volume from own sources | Billed metered | Customer metering inaccuracies
Blackshear | GA2290000 | Pierce | 5811 | 165.173 | 0 | 0 | 158.8202 | 138.787 | 0 | 1.573 | 1.9853 | 142.3453 | 16.4749 | 4.339 | 12.1359 | 20.0332 | 36 | 2243 | 54 | 866186.79 | 4.65 | 360.93 | 10.4701 | 20176.47 | 4380.22 | VPC | 12.61% | 2.983% | 5.2999 | 14.8235 | N/A | 12.1359 | 1.1591 | 77.4597 | Customer retail unit cost (applied to Apparent Losses) | Volume from own sources | Unauthorized consumption
Blairsville | GA2910000 | Union | 4035 | 188.18 | 0 | 0 | 191.6426 | 139.705 | 0 | 3.881 | 2.3955 | 145.9815 | 45.6611 | 6.5312 | 39.1299 | 51.9376 | 74.2625 | 1837 | 98 | 691304 | 6.57 | 505 | 24.2274 | 42910 | 19760.59 | VPC | 27.1% | 9.524% | 9.7407 | N/A | 1443.5975 | 39.1299 | 1.6151 | 85.6731 | Customer retail unit cost (applied to Apparent Losses) | Volume from own sources | Unauthorized consumption
Blakely | GA0990000 | Early | 4855 | 361.301 | 0 | 0 | 361.301 | 209.11 | 0 | 32.9 | 4.5163 | 246.5263 | 114.7747 | 10.2036 | 104.5711 | 152.191 | 54 | 2667 | 51 | 292815 | 4.25 | 36.26 | 12.8851 | 43365.27 | 3791.75 | VPC | 42.12% | 16.57% | 10.4818 | 107.4227 | N/A | 104.5711 | 8.1157 | 64.3235 | Volume from own sources | Customer metering inaccuracies | Billed metered
Blue Ridge Water & Sewer | GA1110000 | Fannin | 6112 | 332.4 | 0 | 11.49 | 321.4835 | 168.49 | 0 | 0.01 | 4.0185 | 172.5185 | 148.9649 | 3.2542 | 145.7107 | 152.9935 | 124.3 | 3315 | 110 | 3128277.84 | 8.53 | 507.97 | 46.964 | 27758.6 | 74016.66 | VPC | 47.59% | 3.319% | 2.6895 | N/A | 3211.6443 | 145.7107 | 3.1026 | 76.783 | Volume from own sources | Unbilled metered | Unauthorized consumption
Bowdon | GA0450000 | Carroll | 6045 | 188.38 | 0 | 0 | 196.2292 | 125.617 | 0 | 2.59 | 2.4529 | 130.6599 | 65.5693 | 5.4546 | 60.1147 | 70.6122 | 140 | 2421 | 77 | 805115 | 5.89 | 268.15 | 31.4931 | 32127.65 | 16119.75 | VPC | 35.98% | 6.161% | 6.1727 | N/A | 1176.4128 | 60.1147 | 1.9088 | 52.9242 | Volume from own sources | Billed metered | Unbilled metered
Braselton | GA1570000 | Jackson | 11443 | 188.38 | 332.347 | 11.879 | 498.8706 | 447.99 | 0 | 16.155 | 6.2359 | 470.3809 | 28.4897 | 16.7222 | 11.7676 | 50.8806 | 125 | 5554 | 112 | 1847400 | 8.22 | 870 | 61.7022 | 137456.09 | 10237.77 | VPC | 10.2% | 9.049% | 8.2489 | 5.8048 | N/A | 11.7676 | 0.19072 | 53.6863 | Water imported | Volume from own sources | Unbilled metered
Bremen | GA1430000 | Haralson | 6200 | 84.64 | 300.166 | 84.409 | 296.9634 | 203.5 | 0 | 1.711 | 3.712 | 208.923 | 88.0404 | 5.4391 | 82.6013 | 93.4634 | 75.5 | 3226 | 90 | 610223 | 5.97 | 610.02 | 29.3139 | 32471.66 | 50388.42 | VPC | 31.47% | 14.12% | 4.6193 | 70.1503 | N/A | 82.6013 | 2.8178 | 78.1089 | Customer metering inaccuracies | Variable production cost (applied to Real Losses) | Unauthorized consumption
Brunswick Glynn Joint Water Sewer Commission - City of Brunswick & North Mainland combined | GA1270000 | Glynn | 36806 | 1753.068 | 0 | 0 | 1706.9796 | 1388.009 | 0 | 9.082 | 21.3372 | 1418.4282 | 288.5513 | 129.2236 | 159.3277 | 318.9706 | 323.5 | 20165 | 54 | 3264074 | 2.89 | 191.89 | 94.113 | 373456.33 | 30573.39 | VPC | 18.69% | 12.56% | 17.557 | 21.6471 | N/A | 159.3277 | 1.6929 | 61.5415 | Volume from own sources | Customer metering inaccuracies | Billed metered
Brunswick Glynn Joint Water Sewer Commission - South Mainland | GA1270150 | Glynn | 2072 | 104.81 | 0 | 0 | 103.1696 | 91.956 | 0 | 2.58 | 1.2896 | 95.8256 | 7.344 | 0.57297 | 6.771 | 11.2136 | 46.8 | 1567 | 54 | 195148 | 2.74 | 191.89 | 9.6232 | 1569.95 | 1299.29 | VPC | 10.87% | 1.851% | 1.0018 | 11.8384 | N/A | 6.771 | 0.70362 | 75.3968 | Customer metering inaccuracies | Billed metered | Volume from own sources
Brunswick Glynn Joint Water Sewer Commisson St Simons | GA1270001 | Glynn | 23579 | 950.691 | 0 | 0 | 954.7966 | 817.489 | 0 | 40.14 | 11.935 | 869.564 | 85.2327 | 79.0071 | 6.2255 | 137.3076 | 145.85 | 11695 | 53 | 1770111 | 2.74 | 191.89 | 49.2001 | 216479.59 | 1194.61 | VPC | 14.38% | 12.86% | 18.5086 | 1.4584 | N/A | 6.2255 | 0.12653 | 68.0283 | Volume from own sources | Customer metering inaccuracies | Billed metered
Buford | GA1350000 | Gwinnett | 8482 | 453.31 | 6.081 | 0 | 468.6422 | 367.432 | 2.322 | 4.9 | 5.858 | 380.512 | 88.1302 | 24.1476 | 63.9826 | 98.8882 | 76 | 3538 | 61 | 2372110.08 | 2.67 | 375.43 | 20.9705 | 64474.12 | 24020.98 | VPC | 21.1% | 3.901% | 18.6992 | 49.5463 | N/A | 63.9826 | 3.0511 | 57.0728 | Volume from own sources | Billed metered | Customer metering inaccuracies
Butts County | GA0350051 | Butts | 21600 | 797.694 | 4.534 | 79.405 | 680.4462 | 618.827 | 0 | 2.047 | 8.5056 | 629.3796 | 51.0666 | 9.5196 | 41.547 | 61.6192 | 280 | 8335 | 74.4 | 3668554 | 5.23 | 595.26 | 75.0877 | 49787.7 | 24731.24 | VPC | 9.056% | 2.203% | 3.1291 | N/A | 406.526 | 41.547 | 0.55331 | 68.9786 | Unbilled metered | Volume from own sources | Variable production cost (applied to Real Losses)
Byron | GA2250000 | Peach | 6419 | 291.132 | 0 | 0 | 288.2495 | 204.108 | 0 | 0.58 | 3.6031 | 208.2911 | 79.9584 | 7.5615 | 72.3969 | 84.1415 | 75.6 | 3358 | 60 | 680232 | 5 | 324.2 | 19.988 | 37807.25 | 23471.09 | VPC | 29.19% | 9.208% | 6.1692 | 59.0672 | N/A | 72.3969 | 3.622 | 51.3327 | Volume from own sources | Customer metering inaccuracies | Variable production cost (applied to Real Losses)
Cairo | GA1310000 | Grady | 9469 | 520.348 | 0 | 0 | 502.7517 | 387.232 | 0 | 0 | 6.2844 | 393.5164 | 109.2353 | 3.1955 | 106.0398 | 115.5197 | 120 | 4471 | 67 | 1458231.62 | 1.75 | 356.83 | 32.2769 | 5592.06 | 37838.19 | VPC | 22.98% | 3.132% | 1.9581 | 64.9788 | N/A | 106.0398 | 3.2853 | 69.4556 | Volume from own sources | Customer retail unit cost (applied to Apparent Losses) | Variable production cost (applied to Real Losses)
Calhoun | GA1290000 | Gordon | 49088 | 3905.6129 | 0 | 662.346 | 3468.7032 | 2159.204 | Note 1 | Note 1 | 43.3588 | 2202.5628 | 1266.1404 | 53.6478 | 1212.4926 | 1309.4992 | 852 | 21414 | 103 | 11317601 | 2.86 | 222.95 | 294.0463 | 153432.84 | 270325.22 | VPC | 37.75% | 3.83% | 6.8638 | N/A | 3898.9407 | 1212.4926 | 4.1235 | 67.136 | Volume from own sources | Variable production cost (applied to Real Losses) | Customer retail unit cost (applied to Apparent Losses)
Camilla | GA2050001 | Mitchell | 5922 | 1155.094 | 0 | 0 | 1155.094 | 914.5145 | Note 1 | Note 1 | 14.4387 | 928.9532 | 226.1408 | 28.6231 | 197.5177 | 240.5795 | 72 | 2743 | 54 | 2241283.24 | 0.95 | 68.07 | 15.7871 | 27191.96 | 13445.03 | VPC | 20.83% | 1.857% | 28.5889 | 197.2819 | N/A | 197.5177 | 12.5113 | 55.4889 | Volume from own sources | Customer metering inaccuracies | Customer retail unit cost (applied to Apparent Losses)
Canton | GA0570001 | Cherokee | 14300 | 1112.09 | 65.834 | 87.478 | 1112.7 | 752.053 | Note 1 | 9.537 | 13.9087 | 775.4987 | 337.2012 | 20.2045 | 316.9967 | 360.647 | 150 | 10300 | 80 | 5507335 | 6.97 | 538.32 | 68.8098 | 140765.65 | 170644.59 | VPC | 32.41% | 5.884% | 5.3743 | 84.3188 | N/A | 316.9967 | 4.6069 | 63.9332 | Volume from own sources | Customer metering inaccuracies | Billed metered
Carroll County | GA0450001 | Carroll | 45380 | 1700.262 | Note 1 | 329.671 | 1370.242 | 1019.745 | 0 | 8.298 | 38.667 | 1066.71 | 303.532 | 16.3592 | 287.1728 | 350.497 | 790.7 | 19485 | 99.9 | 7144165.22 | 7.33 | 360.89 | 262.5531 | 119913.23 | 103637.79 | VPC | 25.58% | 3.366% | 2.3002 | N/A | 995.0358 | 287.1728 | 1.0938 | 73.1824 | Customer metering inaccuracies | Variable production cost (applied to Real Losses) | Billed metered
Carrollton | GA0450002 | Carroll | 25200 | 1922.64 | 0 | 0 | 1922.64 | 1504.139 | 0 | 37.464 | 24.033 | 1565.636 | 357.004 | 8.5669 | 348.4371 | 418.501 | 243 | 9955 | 75 | 4830522.56 | 4.24 | 2.51 | 76.8657 | 36323.86 | 874.58 | VPC | 21.77% | 0.7733% | 2.3577 | 95.8937 | N/A | 348.4371 | 4.5331 | 80.4412 | Volume from own sources | Billed metered | Customer metering inaccuracies
Cartersville | GA0150002 | Bartow | 24830 | 4067.42 | 0 | 1991.633 | 2051.1855 | 1643.797 | 0 | 0 | 25.6398 | 1669.4368 | 381.7486 | 60.0765 | 321.6721 | 407.3885 | 235 | 11363 | 85 | 4274836.89 | 2.47 | 161.81 | 92.3242 | 148574.7 | 52049.76 | VPC | 19.86% | 4.79% | 14.485 | 77.5582 | N/A | 321.6721 | 3.4842 | 67.65 | Volume from own sources | Customer metering inaccuracies | Variable production cost (applied to Real Losses)
Catoosa County | GA0470000 | Catoosa | 50994 | 1434 | 473 | 75 | 1848.943 | 1370 | Note 1 | 0 | 23.1118 | 1393.1118 | 455.8313 | 21.8857 | 433.9455 | 478.943 | 538 | 20638 | 113 | 5568589 | 3.75 | 1200 | 247.729 | 82071.53 | 520734.61 | VPC | 25.9% | 11.32% | 2.9054 | 57.6069 | N/A | 433.9455 | 1.7517 | 74.3305 | Volume from own sources | Unauthorized consumption | Systematic data handling errors
Cave Spring | GA1150000 | Floyd | 4180 | 286.73 | 0 | 110.604 | 156.926 | 76.538 | 0 | 2.571 | 1.9616 | 81.0706 | 75.8554 | 2.4046 | 73.4508 | 80.388 | 87 | 1642 | 102 | 862979.25 | 3.9 | 201.68 | 26.6928 | 9377.87 | 14813.57 | VPC | 51.23% | 2.909% | 4.0121 | N/A | 2313.0481 | 73.4508 | 2.7517 | 64.6678 | Volume from own sources | Billed metered | Variable production cost (applied to Real Losses)
Cedartown | GA2330000 | Polk | 9750 | 511.724 | 0 | 0 | 506.6574 | 356.7116 | 0 | 69.8239 | 6.3332 | 432.8687 | 73.7887 | 8.6539 | 65.1348 | 149.9458 | 85.9 | 4052 | 85 | 787636.33 | 3.08 | 191.4 | 33.2749 | 26653.97 | 12466.8 | VPC | 29.6% | 6.818% | 5.8513 | 44.0404 | N/A | 65.1348 | 1.9575 | 66.8267 | Volume from own sources | Unbilled metered | Customer metering inaccuracies
Centerville | GA1530000 | Houston | 9821 | 383.954 | 10.557 | 0 | 394.4342 | 297.846 | 0 | 5.826 | 4.9304 | 308.6024 | 85.8318 | 11.1226 | 74.7092 | 96.5882 | 48 | 4698 | 65 | 1913375.71 | 4.08 | 396.08 | 22.8799 | 45380.28 | 29590.81 | VPC | 24.49% | 4.141% | 6.4864 | 43.568 | N/A | 74.7092 | 3.2653 | 56.5656 | Volume from own sources | Unbilled metered | Customer metering inaccuracies
Chatsworth | GA2130000 | Murray | 28262 | 632.275 | 546.19 | 3.124 | 1081.6885 | 793.076 | 0 | 20.963 | 13.5211 | 827.5601 | 254.1284 | 12.9095 | 241.2188 | 288.6125 | 426.5 | 11426 | 90.027 | 5168606.56 | 6.82 | 734.22 | 132.1382 | 88042.98 | 177107.7 | VPC | 26.68% | 5.62% | 3.0954 | N/A | 1549.5277 | 241.2188 | 1.8255 | 72.9611 | Volume from own sources | Billed metered | Water imported
Chattooga County | GA0550000 | Chattooga | 7306 | 322.8452 | 7.1572 | 11.212 | 318.5919 | 193.4049 | 0 | 0 | 3.9824 | 197.3873 | 121.2046 | 11.4592 | 109.7454 | 125.187 | 300 | 3494 | 90 | 738267.2 | 8.21 | 472.86 | 70.5322 | 94080.01 | 51894.2 | VPC | 39.29% | 20.03% | 8.9854 | N/A | 1002.241 | 109.7454 | 1.556 | 55.5131 | Volume from own sources | Billed metered | Customer metering inaccuracies
Cherokee County Water & Sewerage Authority | GA0570002 | Cherokee | 189542 | 5983.39 | 27.204 | 375.084 | 5618.1893 | 4726.207 | 0 | 107.446 | 0.428 | 4834.081 | 784.1083 | 81.9405 | 702.1679 | 891.9823 | 1251 | 69730 | 107.31 | 36034112 | 5.68 | 254.13 | 674.7658 | 465421.91 | 178441.92 | VPC | 15.88% | 1.863% | 3.2195 | 27.5885 | N/A | 702.1679 | 1.0406 | 88.1417 | Unauthorized consumption | Variable production cost (applied to Real Losses) | Billed metered
Chickamauga | GA2950000 | Walker | 4150 | 307.801 | 0.27 | 0 | 324.2757 | 107.181 | 0 | 0.315 | 4.0534 | 111.5494 | 212.7263 | 3.2724 | 209.4538 | 217.0947 | 41.9 | 2232 | 165 | 425315.07 | 3.97 | 227.44 | 33.8151 | 12991.58 | 47638.18 | VPC | 66.95% | 14.49% | 4.0168 | 257.0995 | N/A | 209.4538 | 6.1941 | 54.8431 | Volume from own sources | Billed metered | Unbilled metered
Clarkesville | GA1370002 | Habersham | 5785 | 243.888 | 0.98605 | 0 | 227.4682 | 122.6744 | Note 1 | 12.4157 | 2.8434 | 137.9335 | 89.5347 | 34.9288 | 54.6059 | 104.7938 | 60.6 | 2354 | 80.3 | 1213269 | 6.66 | 356.04 | 19.9582 | 232626.08 | 363675.15 | CRUC | 46.07% | 57.52% | 40.6523 | 63.5536 | N/A | 54.6059 | 2.736 | 66.9581 | Volume from own sources | Customer metering inaccuracies | Unbilled metered
Claxton | GA1090001 | Evans | 3840 | 165.217 | 0 | 0 | 173.9126 | 148.606 | 0 | 0 | 2.1739 | 150.7799 | 23.1327 | 2.3074 | 20.8254 | 25.3066 | 43 | 1683 | 60 | 1236190 | 4.74 | 213.55 | 10.6233 | 10936.92 | 4447.25 | VPC | 14.55% | 1.282% | 3.7561 | 33.9012 | N/A | 20.8254 | 1.9604 | 54.3778 | Volume from own sources | Customer retail unit cost (applied to Apparent Losses) | Unauthorized consumption
Clayton | GA2410000 | Rabun | 7225 | 0 | 390.072 | 0 | 390.072 | 173.305 | Note 1 | 4.998 | 4.8759 | 183.1789 | 206.8931 | 10.7928 | 196.1003 | 216.767 | 130 | 3630 | 160 | 2188602 | 12.7 | 3160 | 75.13 | 137068.6987 | 619676.9135 | VPC | 55.57% | 36% | 8.1458 | N/A | 4132.7774 | 196.1003 | 2.6101 | 64.1373 | Water imported | Customer metering inaccuracies | Billed metered
Clayton County Water Authority | GA0630000 | Clayton | 270000 | 9278.254 | 0 | 401.376 | 8720.8873 | 7934.287 | 1.02 | 39.665 | 37.6459 | 8012.6179 | 708.2694 | 22.5843 | 685.6851 | 785.5803 | 1376.98 | 81682 | 92.5 | 33459128 | 3.61 | 472.82 | 665.1807 | 81529.39 | 2475323.14 | CRUC | 9.008% | 8.476% | 0.75751 | 22.9988 | N/A | 685.6851 | 1.0308 | 87.5211 | Volume from own sources | Billed unmetered | Unauthorized consumption
Cleveland Waterworks | GA3110000 | White | 4906 | 163.673 | 78.094 | 0 | 241.767 | 179.111 | 0 | 0.458 | 3.0221 | 182.5911 | 59.1759 | 4.7169 | 54.459 | 62.656 | 40 | 2271 | 90.7 | 1575300 | 2.81 | 1111.18 | 18.4414 | 13254.4 | 60513.8 | VPC | 25.92% | 4.928% | 5.6904 | 65.6992 | N/A | 54.459 | 2.9531 | 61.7255 | Volume from own sources | Water imported | Unbilled metered
Cobb County Water System (Cobb County-Marietta Water Authority) | GA0670003/GA0670002 | Cobb | 533000 | 29792.4 | 0 | 10077.193 | 19865.9252 | 18450.894 | 0 | 0 | 42.031 | 18492.925 | 1373.0002 | 216.5075 | 1156.4927 | 1415.0312 | 3117.8 | 183787 | 110 | 148246450.97 | 5.13 | 2047.2 | 1784.0792 | 1109696.67 | 2367571.78 | VPC | 7.123% | 2.404% | 3.2275 | 17.2399 | N/A | 1156.4927 | 0.64823 | 70.8733 | Volume from own sources | Variable production cost (applied to Real Losses) | Unauthorized consumption
Cochran | GA0230000 | Bleckley | 5244 | 258.0274 | 0 | 0 | 258.0274 | 222.261 | 0.098 | 7.008 | 3.2253 | 232.5923 | 25.435 | 4.6921 | 20.7429 | 35.6684 | 64 | 2685 | 53 | 1355934.22 | 3.49 | 349 | 14.4892 | 16375.52 | 72392.79 | CRUC | 13.82% | 9.181% | 4.7878 | 21.1657 | N/A | 20.7429 | 1.4316 | 64.4825 | Volume from own sources | Billed metered | Variable production cost (applied to Real Losses)
College Park | GA1210002 | Fulton | 20382 | 79.003 | 963.345 | 0 | 1046.3109 | 922.668 | 0 | 19.631 | 13.0789 | 955.3779 | 90.933 | 19.2722 | 71.6608 | 123.6429 | 99.38 | 3419 | 68 | 4551490 | 4.53 | 4240.67 | 26.0733 | 87302.97 | 303889.95 | VPC | 11.82% | 11.64% | 15.4433 | 57.4235 | N/A | 71.6608 | 2.7484 | 70.1926 | Billed metered | Variable production cost (applied to Real Losses) | Customer metering inaccuracies
Columbia County | GA0730000 | Columbia | 101967 | 5390.4 | 0 | 476.771 | 4910.5628 | 4414.5418 | Note 1 | 88.68 | 61.382 | 4564.6038 | 345.959 | 41.852 | 304.107 | 496.021 | 774.88 | 46178 | 44.12 | 6833992.59 | 3.73 | 272.86 | 179.0549 | 156107.89 | 82978.64 | VPC | 10.1% | 4.098% | 2.4831 | 18.0426 | N/A | 304.107 | 1.6984 | 71.267 | Volume from own sources | Variable production cost (applied to Real Losses) | Unauthorized consumption
Columbus | GA2150000 | Muscogee | 229000 | 10641.147 | 4.895 | 1101.397 | 9473.5414 | 7490.926 | 0 | 345.985 | 118.4193 | 7955.3303 | 1518.2111 | 231.0107 | 1287.2004 | 1982.6154 | 1196 | 77374 | 88.7 | 17267333.38 | 2.33 | 272.13 | 585.2344 | 537340.43 | 350285.86 | VPC | 20.93% | 5.872% | 8.1798 | 45.5783 | N/A | 1287.2004 | 2.1995 | 82.489 | Volume from own sources | Variable production cost (applied to Real Losses) | Unauthorized consumption
Commerce | GA1570001 | Jackson | 6819 | 680.89 | 0 | 138.146 | 543.2944 | 293.51 | 0 | 0 | 6.7912 | 300.3012 | 242.9932 | 6.5617 | 236.4315 | 249.7844 | 126.9 | 3872 | 60 | 3253676.37 | 6.55 | 393.55 | 27.7545 | 42979.18 | 93047.62 | VPC | 45.98% | 4.263% | 4.6429 | N/A | 5104.4722 | 236.4315 | 8.5187 | 64.3376 | Volume from own sources | Customer metering inaccuracies | Variable production cost (applied to Real Losses)
Consolidated Utilities, Inc. - Larmonch Utilities | GA0510034 | Chatham | 11799 | 374 | 0 | 0 | 372.1393 | 327 | 0 | 2.9 | 4.6517 | 334.5517 | 37.5876 | 5.5478 | 32.0397 | 45.1393 | 57.2 | 5480 | 49 | 1949159.36 | 5.78 | 319.42 | 20.236 | 32066.56 | 185189.55 | CRUC | 12.13% | 13.39% | 2.7736 | 16.0183 | N/A | 32.0397 | 1.5833 | 57.5882 | Volume from own sources | Unbilled metered | Variable production cost (applied to Real Losses)
Coosa Water Authority | GA2910006 | Union | 3944 | 107.06 | 0 | 0 | 106.5274 | 79.62 | Note 1 | 0.575 | 1.3316 | 81.5266 | 25.0008 | 0.86836 | 24.1324 | 26.9074 | 159 | 3200 | 147 | 71056.25 | 4.36 | 882.71 | 71.9079 | 3786.04 | 21301.92 | VPC | 25.26% | 37.68% | 0.74346 | N/A | 415.8252 | 24.1324 | 0.3356 | 46.134 | Volume from own sources | Billed metered | Unbilled metered
Cordele | GA0810001 | Crisp | 10691 | 719.143 | 0 | 0 | 719.143 | 426.305 | 0 | 0 | 8.9893 | 435.2943 | 283.8487 | 9.5339 | 274.3148 | 292.838 | 132.6 | 6164 | 70 | 1301627 | 3.09 | 808 | 41.9522 | 29459.88 | 221646.33 | VPC | 40.72% | 19.85% | 4.2376 | 121.9253 | N/A | 274.3148 | 6.5387 | 74.1889 | Volume from own sources | Systematic data handling errors | Customer metering inaccuracies
Cornelia | GA1370003 | Habersham | 6130 | 847.73 | 0 | 5.199 | 842.531 | 722.744 | 0 | 5.238 | 10.5316 | 738.5136 | 104.0174 | 11.2665 | 92.7508 | 119.787 | 66.1 | 2538 | 91 | 10567298.34 | 4.25 | 3687 | 24.5227 | 47882.8 | 341972.28 | VPC | 14.22% | 4.239% | 12.162 | 100.1229 | N/A | 92.7508 | 3.7822 | 60.6632 | Volume from own sources | Customer metering inaccuracies | Billed metered
Covington | GA2170001 | Newton | 20379 | 0 | 2289.232 | 1017.997 | 1268.6976 | 918.438 | 0 | 0 | 15.8587 | 934.2967 | 334.4009 | 24.2115 | 310.1894 | 350.2596 | 180 | 8455 | 80 | 5606884 | 5.71 | 2160 | 65.4679 | 138247.5 | 670009.13 | VPC | 27.61% | 15.03% | 7.8454 | 100.5126 | N/A | 310.1894 | 4.738 | 79.2692 | Customer retail unit cost (applied to Apparent Losses) | Customer metering inaccuracies | Unauthorized consumption
Coweta County Water & Sewerage Authority | GA0770042 | Coweta | 68803 | 571.708 | 2255.595 | 268.66 | 2668.2683 | 2479.125 | 0 | 12.535 | 9.1 | 2500.76 | 167.5083 | 20.1205 | 147.3878 | 189.1433 | 1052.1 | 31403 | 110 | 29711323 | 7.69 | 3964.75 | 417.6528 | 154726.52 | 584355.83 | VPC | 7.089% | 2.776% | 1.7554 | N/A | 383.8059 | 147.3878 | 0.3529 | 83.8028 | Unauthorized consumption | Systematic data handling errors | Water imported
Cumming | GA1170000 | Forsyth | 47541 | 2794.45 | 0.3588 | 399.8701 | 2393.6952 | 2124.4326 | 0 | 22.6676 | 1.3464 | 2148.4466 | 245.2487 | 14.7362 | 230.5125 | 269.2626 | 378 | 20732 | 121.68 | 7592771.07 | 4.63 | 480.97 | 228.9403 | 68228.54 | 110869.58 | VPC | 11.25% | 2.511% | 1.9474 | 30.4621 | N/A | 230.5125 | 1.0069 | 75.203 | Volume from own sources | Variable production cost (applied to Real Losses) | Unauthorized consumption
Cusseta and Chattahoochee County (Unified Government) | GA0530002 | Chattahoochee | 3068 | 105.94 | 0 | 0 | 107.0101 | 62.707 | 0 | 12.339 | 1.3376 | 76.3836 | 30.6265 | 1.1826 | 29.4439 | 44.3031 | 61 | 1375 | 65 | 555862.4 | 4.61 | 544.3 | 12.7228 | 5451.63 | 135736.42 | CRUC | 41.4% | 36.74% | 2.3563 | N/A | 1322.4302 | 29.4439 | 2.3143 | 72.4104 | Volume from own sources | Customer metering inaccuracies | Unauthorized consumption
Cuthbert | GA2430000 | Randolph | 3500 | 301.667 | 0 | 0 | 301.667 | 203.45 | 0 | 0 | 3.7708 | 207.2208 | 94.4462 | 21.3842 | 73.0619 | 98.217 | 50 | 1384 | 56 | 382329 | 3.9 | 383.67 | Note 3 | 83398.46 | 28031.68 | VPC | 32.56% | 29.52% | 42.3316 | N/A | 4003.3941 | 73.0619 | Note 3 | 37.3667 | Volume from own sources | Billed metered | Customer metering inaccuracies
Dade County Water & Sewer Authority | GA0830000 | Dade | 36400 | 693.1 | 0 | 0 | 684.5432 | 455.207 | 0 | 0 | 8.5568 | 463.7638 | 220.7794 | 26.8076 | 193.9718 | 229.3362 | 351 | 8494 | 104 | 3051385 | 4.77 | 580.44 | 120.4475 | 127872.44 | 112588.98 | VPC | 33.5% | 8.043% | 8.6468 | N/A | 1514.0443 | 193.9718 | 1.6104 | 78.7148 | Volume from own sources | Unauthorized consumption | Systematic data handling errors
Dahlonega | GA1870000 | Lumpkin | 6214 | 380.999 | 0 | 21.115 | 354.4385 | 255.039 | 0 | 0 | 4.4305 | 259.4695 | 94.969 | 14.9468 | 80.0222 | 99.3995 | 70.1 | 2474 | 150 | 2230467 | 10.73 | 538.83 | 41.0812 | 160379.15 | 43118.36 | VPC | 28.04% | 9.231% | 16.5522 | 88.6172 | N/A | 80.0222 | 1.9479 | 67.5642 | Volume from own sources | Billed metered | Customer retail unit cost (applied to Apparent Losses)
Dallas | GA2230000 | Paulding | 7556 | 9.177 | 219.629 | 0 | 231.5052 | 165.259 | 0 | 1 | 2.8938 | 169.1528 | 62.3524 | 4.0394 | 58.313 | 66.2462 | 38 | 3797 | 89 | 6848620 | 10.96 | 4230 | 25.1801 | 44272.13 | 246664 | VPC | 28.62% | 4.489% | 2.9146 | 42.0758 | N/A | 58.313 | 2.3158 | 80.8986 | Water imported | Variable production cost (applied to Real Losses) | Unauthorized consumption
Dalton | GA3130000 | Whitfield | 99315 | 9922.92 | 157.766 | 231.5886 | 8928.0874 | 6428.3063 | 49.4164 | 38.4094 | 336.0949 | 6852.227 | 2075.8604 | 238.3925 | 1837.4679 | 2450.3647 | 1222.989 | 37241 | 99 | 21426805.95 | 3.21 | 329.2 | 440.9381 | 765239.93 | 604894.45 | VPC | 27.45% | 6.97% | 17.5379 | N/A | 4116.2747 | 1837.4679 | 4.1672 | 73.4027 | Volume from own sources | Customer metering inaccuracies | Unauthorized consumption
Dawson | GA2730001 | Terrell | 4836 | 440.703 | 0 | 0 | 550.8787 | 193.353 | 0 | 0 | 6.886 | 200.239 | 350.6398 | 23.3204 | 327.3194 | 357.5258 | 50 | 2024 | 55 | 1055853 | 3.64 | 481.43 | 11.5251 | 84886.18 | 157581.37 | VPC | 64.9% | 23.28% | 31.5669 | 443.0659 | N/A | 327.3194 | 28.4007 | 35.4833 | Volume from own sources | Billed metered | Customer metering inaccuracies
DeKalb County Department of Watershed Management | GA0890001 | Dekalb | 743000 | 22624.43 | 0 | 52.33 | 24012.8723 | 19800.297 | Note 1 | Note 1 | 300.1609 | 20100.4579 | 3912.4144 | 1151.6538 | 2760.7606 | 4212.5753 | 3036.7 | 196002 | 111.3 | 74359722 | 3.05 | 229.54 | 1861.774 | 3512544.15 | 633704.99 | VPC | 17.54% | 5.669% | 16.0979 | 38.5901 | N/A | 2760.7606 | 1.4829 | 47.8773 | Volume from own sources | Variable production cost (applied to Real Losses) | Customer metering inaccuracies
Demorest | GA1370004 | Habersham | 15130 | 123.19 | 523.553 | 52.089 | 602.1813 | 449.4484 | 0 | 8.897 | 7.5273 | 465.8727 | 136.3086 | 8.4309 | 127.8777 | 152.7329 | 303 | 6942 | 110 | 2728166 | 7.14 | 2193.24 | 107.6233 | 60196.73 | 280466.45 | VPC | 25.36% | 13.81% | 3.3273 | N/A | 1156.27 | 127.8777 | 1.1882 | 53.1237 | Water imported | Customer metering inaccuracies | Billed metered
Douglas | GA0690002 | Coffee | 11872 | 1191.162 | 0 | 0 | 1203.1939 | 1075.156 | 0 | 0 | 15.0399 | 1090.1959 | 112.998 | 62.283 | 50.715 | 128.0379 | 125 | 6454 | 70 | 2781217.63 | 3.58 | 159.39 | 42.0131 | 222973.26 | 8083.46 | VPC | 10.64% | 8.394% | 26.4392 | 21.5285 | N/A | 50.715 | 1.2071 | 75.4921 | Variable production cost (applied to Real Losses) | Billed metered | Customer metering inaccuracies
Douglasville-Douglas County Water and Sewer Authority | GA0970000 | Douglas | 109694 | 4201.591 | 0.424 | 0 | 4038.151 | 3470.971 | 0 | 0 | 50.4769 | 3521.4479 | 516.7031 | 82.0356 | 434.6675 | 567.18 | 944 | 43936 | 98 | 16581670 | 5.77 | 325.24 | 418.4174 | 473345.35 | 141371.27 | VPC | 14.05% | 3.806% | 5.1155 | 27.1047 | N/A | 434.6675 | 1.0388 | 78.234 | Billed metered | Volume from own sources | Unauthorized consumption
Dublin | GA1750002 | Laurens | 17500 | 1190.831 | 0 | 0 | 1190.831 | 692.895 | Note 1 | 7.628 | 14.8854 | 715.4084 | 475.4226 | 41.5789 | 433.8437 | 497.936 | 230.6 | 7299 | 62 | 3596986 | 6.66 | 332.21 | 53.0084 | 276915.78 | 144127.2 | VPC | 41.81% | 11.91% | 15.6069 | N/A | 5154.4353 | 433.8437 | 8.1844 | 64.0784 | Volume from own sources | Customer metering inaccuracies | Unbilled metered
East Dublin | GA1750004 | Laurens | 4701 | 152.533 | 0 | 0 | 154.8558 | 86.021 | 0 | 0.2 | 3.225 | 89.446 | 65.4098 | 2.3618 | 63.048 | 68.8348 | 40 | 1382 | 65 | 390000 | 3.52 | 241.86 | Note 3 | 8313.55 | 15248.8 | VPC | 44.45% | 6.254% | 4.6821 | 124.9887 | N/A | 63.048 | Note 3 | 62.0943 | Volume from own sources | Billed metered | Customer retail unit cost (applied to Apparent Losses)
East Point Water Treatment plant | GA1210003 | Fulton | 33712 | 1052.295 | 0 | 603.28 | 449.015 | 144 | 0 | 1.385 | 5.6127 | 150.9977 | 298.0173 | 2.9511 | 295.0662 | 305.015 | 176 | 11631 | 89 | 351969 | 3.91 | 415.25 | 87.6059 | 11538.69 | 1153709 | CRUC | 67.93% | 338.8% | 0.69514 | 69.504 | N/A | 295.0662 | 3.3681 | 68.7272 | Volume from own sources | Customer metering inaccuracies | Customer retail unit cost (applied to Apparent Losses)
Eastman | GA0910002 | Dodge | 7073 | 349.029 | 0 | 0 | 306.5961 | 223.207 | Note 1 | 14.8 | 3.8325 | 241.8395 | 64.7566 | 6.1818 | 58.5749 | 83.3891 | 64.8 | 3405 | 60 | 1382076 | 1.29 | 389.19 | 18.8629 | 7974.51 | 75561.56 | CRUC | 27.2% | 7.783% | 4.974 | 47.1304 | N/A | 58.5749 | 3.1053 | 52.898 | Volume from own sources | Billed metered | Customer metering inaccuracies
Eatonton Putnam Water & Sewer Authority | GA2370000 | Putnam | 12561 | 0 | 348.115 | 9.0622 | 339.0528 | 231.383 | 0 | 22.4633 | 4.2382 | 258.0845 | 80.9684 | 7.935 | 73.0334 | 107.6698 | 240 | 8803 | 65 | 2743382 | 4.35 | 2966.47 | 62.1322 | 34517.11 | 216651.37 | VPC | 31.76% | 12.04% | 2.4696 | 22.7299 | N/A | 73.0334 | 1.1755 | 73.7907 | Customer metering inaccuracies | Customer retail unit cost (applied to Apparent Losses) | Variable production cost (applied to Real Losses)
Effingham County Surface Water System | GA1030131 | Effingham | 9869 | 0 | 762.042 | 0 | 758.2507 | 643.613 | Note 1 | 103.048 | 0.01 | 746.671 | 11.5797 | 0.67809 | 10.9017 | 114.6377 | 94.7 | 3735 | 45 | 1171349 | 2.02 | 1537.12 | 17.6171 | 1369.74 | 22021.35 | CRUC | 15.12% | 19.77% | 0.4974 | 7.9967 | N/A | 10.9017 | 0.61881 | 75.2561 | Billed metered | Total annual cost of operating water system | Water imported
Elberton | GA1050001 | Elbert | 7800 | 519.03 | 0 | 0 | 527.8987 | 462.707 | 0.534 | 6.037 | 6.5987 | 475.8767 | 52.022 | 10.6315 | 41.3905 | 64.6577 | 122.43 | 3861 | 73 | 1574996 | 4.27 | 520.53 | 33.0797 | 45396.45 | 21544.99 | VPC | 12.25% | 4.668% | 7.544 | N/A | 926.2319 | 41.3905 | 1.2512 | 80.281 | Volume from own sources | Billed metered | Unauthorized consumption
Ellijay Gilmer County Water and Sewerage Authority | GA1230000 | Gilmer | 13010 | 939.154 | 0 | 0 | 935.7852 | 713.951 | Note 1 | 51.622 | 0.22 | 765.793 | 169.9922 | 9.1868 | 160.8054 | 221.8342 | 240 | 6057 | 95 | 2589997 | 4.66 | 481.77 | 76.526 | 42810.32 | 77471.22 | VPC | 23.71% | 5.608% | 4.1554 | N/A | 1835.6782 | 160.8054 | 2.1013 | 86.8824 | Volume from own sources | Unauthorized consumption | Customer metering inaccuracies
Etowah Water & Sewer Authority | GA0850007 | Dawson | 13843 | 529.55 | 1.905 | 12.737 | 524.0607 | 395.211 | 0 | 1.618 | 6.5508 | 403.3798 | 120.681 | 2.2982 | 118.3828 | 128.8497 | 191.19 | 6063 | 99 | 3561592.89 | 13.55 | 341.96 | 70.2388 | 31140.33 | 40482.18 | VPC | 24.59% | 2.089% | 1.0385 | N/A | 1696.4087 | 118.3828 | 1.6854 | 81.3418 | Volume from own sources | Unauthorized consumption | Systematic data handling errors
Fairburn | GA1210004 | Fulton | 13693 | 0 | 486.747 | 0 | 492.9084 | 375.554 | 0 | 0 | 6.1614 | 381.7154 | 111.193 | 5.9646 | 105.2284 | 117.3544 | 71.49 | 6155 | 75 | 3575226 | 6.46 | 4950 | 35.8615 | 38531.51 | 520880.43 | VPC | 23.81% | 16.5% | 2.655 | 46.8395 | N/A | 105.2284 | 2.9343 | 73.2358 | Water imported | Billed metered | Customer metering inaccuracies
Fayette County Water System | GA1130001 | Fayette | 77051 | 3356.484 | 9.3964 | 252.4538 | 3240.1435 | 2801.7803 | 1.9398 | 1.038 | 40.5018 | 2845.2599 | 394.8836 | 72.3052 | 322.5784 | 436.4233 | 642 | 39224 | 93 | 15931846 | 3.62 | 463.13 | 317.6173 | 261744.76 | 149394.14 | VPC | 13.47% | 2.701% | 5.0504 | 22.5315 | N/A | 322.5784 | 1.0156 | 70.5783 | Volume from own sources | Customer metering inaccuracies | Customer retail unit cost (applied to Apparent Losses)
Fayetteville | GA1130003 | Fayette | 15281 | 248.446 | 251.776 | 0 | 500.222 | 425.202 | 0 | 0 | 6.2528 | 431.4548 | 68.7672 | 6.6085 | 62.1587 | 75.02 | 93.1 | 7945 | 60 | 2781880 | 3.35 | 1359 | 37.1297 | 22138.57 | 84473.67 | VPC | 15% | 4.138% | 2.2789 | 21.4346 | N/A | 62.1587 | 1.6741 | 69.1799 | Volume from own sources | Customer metering inaccuracies | Billed metered
Fitzgerald | GA0170000 | Ben Hill | 12935 | 736.367 | 0 | 0 | 714.9194 | 639.405 | Note 1 | 8.407 | 8.9365 | 656.7485 | 58.1709 | 13.3177 | 44.8532 | 75.5144 | 130 | 5924 | 63 | 1030263.9 | 2.12 | 134.73 | 36.6057 | 28233.62 | 6043.07 | VPC | 10.56% | 3.554% | 6.1592 | 20.7437 | N/A | 44.8532 | 1.2253 | 57.7569 | Volume from own sources | Unbilled metered | Billed metered
Floyd County | GA1150001 | Floyd | 41738 | 1266.711 | 546.321 | 32.659 | 1745.4637 | 1355.987 | 0 | 19.882 | 23 | 1398.869 | 346.5947 | 47.7536 | 298.8411 | 389.4767 | 587 | 18564 | 80 | 6815276 | 4.43 | 497.2 | 174.0399 | 211548.57 | 148583.79 | VPC | 22.31% | 5.597% | 7.0476 | N/A | 1394.7917 | 298.8411 | 1.7171 | 72.7219 | Volume from own sources | Water imported | Unauthorized consumption
Folkston | GA0490000 | Charlton | 5940 | 251.072 | 0 | 1.575 | 252.2094 | 231.385 | 0 | 0.991 | 3.1526 | 235.5286 | 16.6808 | 3.5562 | 13.1245 | 20.8244 | 58.8 | 2324 | 52 | 551898 | 2.94 | 273.87 | 12.6541 | 10455.28 | 3594.42 | VPC | 8.257% | 2.751% | 4.1924 | 15.4723 | N/A | 13.1245 | 1.0372 | 67.4749 | Unbilled metered | Customer metering inaccuracies | Billed metered
Forsyth | GA2070001 | Monroe | 7400 | 481.87 | 0 | 9.523 | 477.8288 | 447.567 | Note 1 | Note 1 | 5.9729 | 453.5399 | 24.289 | 6.8344 | 17.4546 | 30.2618 | 50 | 3079 | 60 | 1487853 | 5.01 | 515.5 | 16.0385 | 34240.19 | 8997.84 | VPC | 6.333% | 3.113% | 6.0813 | 15.5313 | N/A | 17.4546 | 1.0883 | 65.4346 | Volume from own sources | Customer metering inaccuracies | Billed metered
Forsyth County Water and Sewer | GA1170050 | Forsyth | 138368 | 4996 | 400.648 | 420.834 | 4997.7321 | 4325.204 | 0 | 2.694 | 62.4717 | 4390.3697 | 607.3625 | 67.0235 | 540.339 | 672.5281 | 1067.5 | 61718 | 114 | 30906358.69 | 5.92 | 1032.55 | 625.5179 | 396825.34 | 557927.02 | VPC | 13.46% | 3.307% | 2.9752 | 23.9862 | N/A | 540.339 | 0.86383 | 70.0784 | Volume from own sources | Customer metering inaccuracies | Billed metered
Fort Oglethorpe | GA0470001 | Catoosa | 9446 | 0 | 303 | 0 | 303 | 191 | Note 1 | 0 | 3.7875 | 194.7875 | 108.2125 | 5.133 | 103.0795 | 112 | 38 | 3242 | 110 | 1717121 | 7.83 | 1.62 | 27.779 | 40191.07 | 807112.8 | CRUC | 36.96% | 51.07% | 4.3377 | 87.1097 | N/A | 103.0795 | 3.7107 | 79.9222 | Billed metered | Customer metering inaccuracies | Unauthorized consumption
Fort Valley Utility Commission | GA2250001 | Peach | 16430 | 509.084 | 0 | 0 | 514.2263 | 450.398 | Note 1 | Note 1 | 6.4278 | 456.8258 | 57.4004 | 15.2154 | 42.185 | 63.8283 | 153 | 5341 | 55 | 2036997 | 4.46 | 376.96 | 32.6998 | 67935.71 | 15902.07 | VPC | 12.41% | 4.235% | 7.8049 | 21.6393 | N/A | 42.185 | 1.2901 | 57.364 | Volume from own sources | Customer metering inaccuracies | Systematic data handling errors
Franklin County | GA1190051 | Franklin | 3934 | 247.524 | 82.645 | 80.128 | 250.5608 | 171.5603 | 0 | 0.95732 | 3.132 | 175.6496 | 74.9112 | 5.4788 | 69.4323 | 79.0005 | 232 | 2093 | 125 | 1801130.81 | 4.07 | 1907.75 | 71.5888 | 22298.85 | 132459.52 | VPC | 31.53% | 9.025% | 7.1718 | N/A | 819.9377 | 69.4323 | 0.96988 | 54.8023 | Volume from own sources | Customer metering inaccuracies | Billed metered
Gainesville | GA1390001 | Hall | 140000 | 6847 | 0 | 0 | 6841 | 6094 | Note 1 | Note 1 | 49.42 | 6143.42 | 697.58 | 239.3853 | 458.1947 | 747 | 1462 | 57306 | 121 | 28729450 | 5.52 | 533 | 728.9575 | 1321406.73 | 244217.79 | VPC | 10.92% | 5.541% | 11.4447 | 21.9057 | N/A | 458.1947 | 0.62856 | 75.7716 | Volume from own sources | Billed metered | Unauthorized consumption
Garden City | GA0510000 | Chatham | 8141 | 317.426 | 0 | 0 | 306.726 | 252.688 | Note 1 | 17.269 | 1.652 | 271.609 | 35.117 | 6.9079 | 28.2091 | 54.038 | 51 | 3585 | 55 | 1024119.02 | 6 | 199.22 | 16.3342 | 41447.17 | 5619.82 | VPC | 17.62% | 4.964% | 5.2791 | 21.558 | N/A | 28.2091 | 1.727 | 49.131 | Volume from own sources | Variable production cost (applied to Real Losses) | Total annual cost of operating water system
Glen of Robin Hood | GA0510109 | Chatham | 5000 | 207.593 | 0 | 0 | 230.6589 | 154.955 | 0 | 0 | 2.8832 | 157.8382 | 72.8207 | 10.8548 | 61.9659 | 75.7039 | 27.7 | 2461 | 45 | 620522 | 1.75 | 377.53 | 8.5247 | 18995.86 | 23393.98 | VPC | 32.82% | 7.007% | 12.0842 | 68.984 | N/A | 61.9659 | 7.269 | 72.4535 | Volume from own sources | Customer metering inaccuracies | Unauthorized consumption
Glennville | GA2670002 | Tattnall | 5173 | 246.605 | 0 | 0 | 245.4758 | 213.142 | 0 | 14.871 | 3.0684 | 231.0814 | 14.3944 | 2.2923 | 12.102 | 32.3338 | 52 | 2112 | 50 | 828346 | 3.89 | 209.9 | 10.9157 | 8917.2 | 2540.22 | VPC | 13.17% | 1.838% | 2.9737 | 15.699 | N/A | 12.102 | 1.1087 | 80.2862 | Volume from own sources | Total annual cost of operating water system | Unauthorized consumption
Gray | GA1690000 | Jones | 8885 | 112.5593 | 98.443 | 3.149 | 208.6467 | 148.0792 | 0 | 7.204 | 2.6081 | 157.8912 | 50.7555 | 4.0609 | 46.6946 | 60.5676 | 60.56 | 2170 | 50 | 693344 | 6.69 | 2088.57 | 11.9196 | 27167.15 | 97525.01 | VPC | 29.03% | 20.94% | 5.127 | 58.9542 | N/A | 46.6946 | 3.9175 | 56.1588 | Water imported | Billed metered | Unbilled metered
Greensboro | GA1330000 | Greene | 3156 | 220.924 | 0 | 0 | 227.7567 | 175.248 | 0 | 0 | 2.847 | 178.095 | 49.6617 | 1.3075 | 48.3542 | 52.5087 | 41.4 | 1628 | 75 | 899210.97 | 8.47 | 606.53 | Note 3 | 11074.62 | 409560.33 | CRUC | 23.05% | 49.46% | 2.2004 | 81.3743 | N/A | 48.3542 | Note 3 | 66.2275 | Volume from own sources | Billed metered | Customer retail unit cost (applied to Apparent Losses)
Griffin | GA2550000 | Spalding | 23643 | 3235.12 | 0 | 1941.32 | 1233.6572 | 726.521 | 0 | 43.403 | 15.4207 | 785.3447 | 448.3125 | 14.2517 | 434.0608 | 507.1362 | 212.8 | 10918 | 73 | 7098482 | 7.62 | 323.51 | 74.3115 | 108598.33 | 140423.87 | VPC | 41.11% | 3.776% | 3.5763 | 108.9217 | N/A | 434.0608 | 5.8411 | 80.2893 | Volume from own sources | Variable production cost (applied to Real Losses) | Unauthorized consumption
Grovetown | GA0730001 | Columbia | 12165 | 13.921 | 336.68 | 0 | 350.5976 | 291.5622 | 0 | 0 | 4.3825 | 295.9447 | 54.6529 | 7.5556 | 47.0973 | 59.0354 | 68.5 | 6383 | 80 | 1956215.29 | 6.35 | 1800.19 | 38.7786 | 47978.37 | 84784.09 | VPC | 16.84% | 7.19% | 3.2431 | 20.2152 | N/A | 47.0973 | 1.2145 | 71.1104 | Customer metering inaccuracies | Customer retail unit cost (applied to Apparent Losses) | Variable production cost (applied to Real Losses)
Gwinnett County | GA1350004 | Gwinnett | 795657 | 25645.158 | 0 | 696.913 | 24937.872 | 22458.615 | 0 | 9.8703 | 29.9038 | 22498.3891 | 2439.4829 | 322.4391 | 2117.0438 | 2479.257 | 3788.2 | 261278 | 112 | 22047850 | 5.36 | 241.85 | 2439.958 | 1728273.52 | 512007.05 | VPC | 9.942% | 10.2% | 3.3811 | 22.199 | N/A | 2117.0438 | 0.86766 | 73.9459 | Volume from own sources | Unauthorized consumption | Systematic data handling errors
Hampton | GA1510000 | Henry | 7305 | 40.351 | 180.872 | 0 | 226.7783 | 150.4425 | Note 1 | Note 1 | 2.8347 | 153.2772 | 73.5011 | 1.8512 | 71.6499 | 76.3358 | 41.08 | 3033 | 54 | 1075108 | 5.73 | 3140.23 | 13.3475 | 10607.12 | 224997.24 | VPC | 33.66% | 22.74% | 1.6722 | 64.7218 | N/A | 71.6499 | 5.3681 | 58.3072 | Water imported | Customer metering inaccuracies | Billed metered
Hapeville | GA1210006 | Fulton | 6500 | 0 | 334.957 | 0 | 335.1246 | 239.017 | 0 | 0.77 | 4.1891 | 243.9761 | 91.1485 | 6.329 | 84.8195 | 96.1076 | 24.1 | 2351 | 75 | 2770501.61 | 8.78 | 7571.24 | 13.223 | 55568.32 | 744715.55 | CRUC | 28.68% | 30.46% | 7.3754 | 98.844 | N/A | 84.8195 | 6.4146 | 57.2479 | Water imported | Customer metering inaccuracies | Total annual cost of operating water system
Haralson County Water Authority | GA1430007 | Haralson | 12220 | 828.242 | 79.582 | 497.695 | 399.4372 | 273.008 | 0 | 0.389 | 4.993 | 278.39 | 121.0472 | 25.4548 | 95.5924 | 126.4292 | 389.5 | 5210 | 89.6 | 2806054 | 5.73 | 570.24 | 94.4719 | 145855.8 | 54510.64 | VPC | 31.65% | 7.25% | 13.3856 | N/A | 672.3931 | 95.5924 | 1.0119 | 79.5627 | Billed metered | Customer metering inaccuracies | Unauthorized consumption
Harlem | GA0730002 | Columbia | 6099 | 0 | 173.601 | 0 | 171.0355 | 132.111 | 0.012 | 4.81 | 2.1379 | 139.0709 | 31.9645 | 3.5522 | 28.4124 | 38.9125 | 69 | 2300 | 70 | 968292 | 7.86 | 1841 | 18.3523 | 27920.07 | 52307.14 | VPC | 22.75% | 9.606% | 4.2313 | 33.8444 | N/A | 28.4124 | 1.5482 | 63.2931 | Water imported | Billed metered | Unbilled metered
Harris County Waterworks | GA1450011 | Harris | 20062 | 648.42 | 221.2553 | 1.3816 | 865.5874 | 726.0561 | 0 | 0.040701 | 10.8198 | 736.9167 | 128.6708 | 22.597 | 106.0738 | 139.5313 | 405.7 | 8474 | 92.7053 | 3735437.2 | 5.38 | 982.13 | 117.2784 | 121487.24 | 104178.67 | VPC | 16.12% | 6.327% | 7.3058 | N/A | 716.3253 | 106.0738 | 0.90446 | 63.2996 | Water imported | Unbilled metered | Customer metering inaccuracies
Hart County Water and Sewer Authority | GA1470065 | Hart | 4059 | 0 | 286 | 21 | 267.793 | 238 | 0 | 0 | 3.3474 | 241.3474 | 26.4456 | 7.367 | 19.0785 | 29.793 | 148 | 2135 | 95 | 2210275 | 4.45 | 1984 | 38.8682 | 32783.36 | 84899.38 | CRUC | 11.13% | 5.998% | 9.4537 | N/A | 353.175 | 19.0785 | 0.49085 | 63.1641 | Water imported | Customer retail unit cost (applied to Apparent Losses) | Billed metered
Hartwell | GA1470000 | Hart | 7116 | 484.828 | 0 | 124.7341 | 355.3014 | 272.6781 | 0 | 22.48 | 3.4422 | 298.6003 | 56.7011 | 9.7604 | 46.9408 | 82.6233 | 85.115 | 2853 | 74.126 | 1271846.72 | 4.82 | 331.42 | 24.0371 | 47029.85 | 15557.11 | VPC | 23.25% | 5.596% | 9.3728 | 45.077 | N/A | 46.9408 | 1.9528 | 54.5356 | Volume from own sources | Customer metering inaccuracies | Unbilled metered
Hawkinsville | GA2350001 | Pulaski | 6650 | 349.65 | 0 | 0 | 349.699 | 233.287 | 0 | 3.359 | 4.3712 | 241.0172 | 108.6817 | 1.9792 | 106.7025 | 116.412 | 60 | 2003 | 55 | 721723.04 | 3.45 | 406.22 | 12.5479 | 6828.36 | 43344.68 | VPC | 33.29% | 7.387% | 2.7072 | 145.9489 | N/A | 106.7025 | 8.5036 | 76.8696 | Customer metering inaccuracies | Volume from own sources | Billed metered
Hazlehurst | GA1610001 | Jeff Davis | 5504 | 306.359 | 0 | 0 | 306.359 | 189.883 | 8.923 | 7.743 | 8.14 | 214.689 | 91.67 | 12.2777 | 79.3923 | 107.553 | 77 | 3082 | 51 | 903797 | 2.68 | 214.96 | 16.3602 | 32904.26 | 17066.17 | VPC | 35.11% | 5.907% | 10.9142 | 70.5753 | N/A | 79.3923 | 4.8528 | 80.3421 | Volume from own sources | Unauthorized consumption | Systematic data handling errors
Heard County Water Authority | GA1490000 | Heard | 8172 | 553.26 | Note 1 | 52.521 | 501.7922 | 259.794 | Note 1 | 5.55 | 6.2724 | 271.6164 | 230.1758 | 7.3191 | 222.8566 | 241.9982 | 400 | 3783 | 80 | 1738192 | 6.41 | 751.7 | 79.7583 | 46915.75 | 167521.34 | VPC | 48.23% | 12.85% | 5.3007 | N/A | 1526.4154 | 222.8566 | 2.7941 | 70.0166 | Customer metering inaccuracies | Customer retail unit cost (applied to Apparent Losses) | Variable production cost (applied to Real Losses)
Henry County Water Authority | GA1510001 | Henry | 218667 | 5673.363 | 44.5144 | 440.6888 | 5261.6905 | 4588.6584 | 0 | 85.2908 | 23.9628 | 4697.912 | 563.7785 | 153.5405 | 410.238 | 673.0321 | 1333.1 | 68574 | 101 | 34025801 | 8.27 | 319.44 | 645.0701 | 1270087.09 | 131046.42 | VPC | 12.79% | 4.22% | 6.1344 | 16.3902 | N/A | 410.238 | 0.63596 | 85.2204 | Volume from own sources | Unauthorized consumption | Billed metered
Hephzibah | GA2450002 | Richmond | 4500 | 209.903 | 0 | 0 | 209.903 | 161.4813 | 0 | 0 | 2.6238 | 164.1051 | 45.7979 | 5.069 | 40.7289 | 48.4217 | 50.4 | 1690 | 70 | 530420.2 | 1.55 | 686.41 | 13.4435 | 7856.96 | 27956.75 | VPC | 23.07% | 7.091% | 8.2176 | 66.0273 | N/A | 40.7289 | 3.0296 | 51.6667 | Volume from own sources | Customer metering inaccuracies | Customer retail unit cost (applied to Apparent Losses)
Hiawassee | GA2810000 | Towns | 5496 | 409.33 | 0 | 211.683 | 198.7516 | 101.4025 | 0 | 0.245 | 2.4844 | 104.1319 | 94.6197 | 1.0562 | 93.5634 | 97.3491 | 75.4 | 2526 | 95 | 1787199.14 | 2.28 | 821 | 27.2828 | 2408.24 | 76815.59 | VPC | 48.98% | 4.558% | 1.1456 | 101.4799 | N/A | 93.5634 | 3.4294 | 81.2912 | Variable production cost (applied to Real Losses) | Unauthorized consumption | Systematic data handling errors
Hinesville | GA1790000 | Liberty | 24666 | 1122.178 | 0 | 0 | 1111.0673 | 962.9983 | 0.2484 | 8.6895 | 13.8883 | 985.8245 | 125.2428 | 7.6205 | 117.6224 | 147.8206 | 191.58 | 13990 | 52 | 1923213 | 4.99 | 134.56 | 59.5013 | 38026.15 | 15827.26 | VPC | 13.3% | 2.958% | 1.4924 | 23.0345 | N/A | 117.6224 | 1.9768 | 85.9495 | Volume from own sources | Unauthorized consumption | Systematic data handling errors
Hogansville | GA2850000 | Troup | 3866 | 0 | 182.2574 | 24.7495 | 157.5079 | 106.6407 | 0 | 0 | 1.9688 | 108.6095 | 48.8983 | 6.273 | 42.6253 | 50.8672 | 31.3 | 1835 | 100 | 468185.26 | 3.54 | 1196.99 | Note 3 | 22206.56 | 51022.05 | VPC | 32.3% | 16.14% | 9.3659 | 63.6412 | N/A | 42.6253 | Note 3 | 57.6853 | Water imported | Customer metering inaccuracies | Billed metered
Homerville | GA0650000 | Clinch | 3234 | 142.304 | 0 | 0 | 142.304 | 104.341 | Note 1 | 12.107 | 1.7788 | 118.2268 | 24.0772 | 10.7425 | 13.3347 | 37.963 | 45 | 1591 | 45 | 403737.31 | 3.65 | 0.41 | 7.9185 | 39210.22 | 5.47 | VPC | 26.68% | 9.715% | 18.4988 | 22.9625 | N/A | 13.3347 | 1.684 | 51.4118 | Volume from own sources | Customer retail unit cost (applied to Apparent Losses) | Unbilled metered
Houston County | GA1530021 | Houston | 67746 | 4769.447 | 0 | 0 | 4673.6374 | 3635.6913 | 35.6 | 0.595 | 58.4205 | 3730.3068 | 943.3307 | 145.2547 | 798.0759 | 1002.3461 | 398.2 | 19240 | 64 | 6611356.27 | 1.77 | 299.29 | 117.7405 | 257100.88 | 238856.15 | VPC | 21.45% | 7.769% | 20.6839 | 113.6439 | N/A | 798.0759 | 6.7783 | 55.9032 | Volume from own sources | Customer retail unit cost (applied to Apparent Losses) | Billed metered
Jackson County | GA1570117 | Jackson | 19191 | 0 | 1206.4894 | 340.7996 | 866.2342 | 614.3437 | 0 | 185.9556 | 10.8279 | 811.1272 | 55.107 | 13.9139 | 41.1931 | 251.8905 | 420.16 | 12466 | 104.16 | 8913112 | 7.92 | 2692 | 157.5089 | 110198.03 | 110891.73 | VPC | 29.08% | 8.424% | 3.0579 | N/A | 268.6065 | 41.1931 | 0.26153 | 74.214 | Water imported | Billed metered | Customer metering inaccuracies
Jasper | GA2270000 | Pickens | 9850 | 666.81 | 9.242 | 52.778 | 623.4109 | 364.289 | 0 | 5.898 | 7.7926 | 377.9796 | 245.4313 | 45.9969 | 199.4344 | 259.1219 | 184.1 | 6287 | 70 | 3087340 | 3.25 | 477.73 | 54.1057 | 149489.97 | 95275.79 | VPC | 41.57% | 8.14% | 20.0444 | 86.9088 | N/A | 199.4344 | 3.686 | 62.661 | Total annual cost of operating water system | Volume from own sources | Billed metered
Jefferson | GA1570003 | Jackson | 10501 | 489.81 | 19.067 | 0 | 501.5568 | 400.316 | 0.324 | 16.794 | 6.2695 | 423.7035 | 77.8533 | 6.4679 | 71.3854 | 100.9168 | 120.75 | 4966 | 66 | 2205503.08 | 10.9 | 587.2 | 33.6816 | 70500.27 | 41917.52 | VPC | 20.12% | 5.711% | 3.5683 | 39.3831 | N/A | 71.3854 | 2.1194 | 80.5307 | Variable production cost (applied to Real Losses) | Volume from own sources | Customer metering inaccuracies
Jesup | GA3050000 | Wayne | 10200 | 448.235 | 0 | 0 | 442.7012 | 356.249 | Note 1 | 16.351 | 5.5338 | 378.1338 | 64.5675 | 13.5211 | 51.0464 | 86.4522 | 134 | 4221 | 58.6 | 1052674.15 | 3.52 | 202.67 | 29.0482 | 47594.23 | 10345.57 | VPC | 19.53% | 5.925% | 8.7761 | N/A | 1043.6799 | 51.0464 | 1.7573 | 76.9568 | Variable production cost (applied to Real Losses) | Volume from own sources | Billed metered
Jones County Water System | GA1690002 | Jones | 10911 | 553.308 | 0 | 98.781 | 468.5845 | 298.001 | 0 | 26.719 | 5.8573 | 330.5773 | 138.0072 | 30.153 | 107.8542 | 170.5835 | 157 | 4016 | 77 | 1800000 | 3.64 | 0.79 | 40.802 | 109756.87 | 85.68 | VPC | 36.4% | 6.104% | 20.5704 | N/A | 1882.1088 | 107.8542 | 2.6434 | 59.4969 | Volume from own sources | Unbilled metered | Billed metered
Kingsland | GA0390000 | Camden | 18697 | 601.139 | 0 | 0 | 598.1483 | 525.324 | 0 | 0.822 | 7.4769 | 533.6229 | 64.5254 | 8.1233 | 56.4021 | 72.8243 | 179 | 9351 | 62 | 1705055 | 2.27 | 215.37 | 53.6566 | 18439.86 | 12147.32 | VPC | 12.17% | 1.899% | 2.38 | 16.5251 | N/A | 56.4021 | 1.0512 | 71.1602 | Billed metered | Customer metering inaccuracies | Variable production cost (applied to Real Losses)
LaFayette | GA2950002 | Walker | 18177 | 740.034 | 296.989 | 0 | 1047.3776 | 669.816 | Note 1 | 2.913 | 13.0922 | 685.8212 | 361.5564 | 12.6016 | 348.9548 | 377.5616 | 238.8 | 8145 | 75 | 3366846.54 | 4.7 | 594.4 | 68.8114 | 59227.72 | 207418.7 | VPC | 36.05% | 8.202% | 4.2388 | 117.3776 | N/A | 348.9548 | 5.0712 | 67.3385 | Customer metering inaccuracies | Volume from own sources | Unbilled metered
LaGrange | GA2850001 | Troup | 41852 | 2553.89 | 0 | 166.611 | 2387.279 | 1921.032 | Note 1 | Note 1 | 29.841 | 1950.873 | 436.406 | 15.5854 | 420.8206 | 466.247 | 447 | 19980 | 89 | 5027016 | 4.19 | 411.93 | 175.915 | 65302.8 | 173348.64 | VPC | 19.53% | 4.992% | 2.1371 | 57.7044 | N/A | 420.8206 | 2.3922 | 69.7111 | Volume from own sources | Variable production cost (applied to Real Losses) | Unauthorized consumption
Lake Blackshear Area Water System | GA0810064 | Crisp | 3505 | 97.935 | 0 | 0 | 97.935 | 74.91 | 0 | 0 | 1.2242 | 76.1342 | 21.8008 | 0.54465 | 21.2562 | 23.025 | 110 | 1636 | 62 | 535711 | 3 | 463.85 | 19.0205 | 1633.94 | 9859.67 | VPC | 23.51% | 2.251% | 0.91209 | N/A | 529.4188 | 21.2562 | 1.1175 | 66.5333 | Volume from own sources | Billed metered | Customer metering inaccuracies
Lakeland | GA1730000 | Lanier | 5971 | 103.464 | 0 | 0 | 121.7224 | 76.497 | 0 | 40.466 | 1.5215 | 118.4845 | 3.2378 | 1.1661 | 2.0718 | 45.2254 | 24.8 | 1664 | 40 | 317613.53 | 3 | 362.86 | Note 3 | 3498.18 | 751.76 | VPC | 37.15% | 6.135% | 1.9199 | 3.4111 | N/A | 2.0718 | Note 3 | 53.4663 | Volume from own sources | Variable production cost (applied to Real Losses) | Total annual cost of operating water system
Lavonia | GA1190003 | Franklin | 8190 | 432.04 | 20.911 | 133.99 | 314.7322 | 198.056 | 0 | 11.556 | 3.9342 | 213.5462 | 101.186 | 3.3993 | 97.7867 | 116.6762 | 127 | 3575 | 107 | 1521656 | 8.55 | 642.02 | 47.7768 | 29063.7 | 62781.05 | VPC | 37.07% | 6.689% | 2.605 | N/A | 2109.5189 | 97.7867 | 2.0467 | 63.1797 | Volume from own sources | Water exported | Unauthorized consumption
Lawrenceville | GA1350005 | Gwinnett | 30000 | 157.394 | 646.652 | 5.021 | 807.4576 | 658.518 | Note 1 | 69.752 | 10.0932 | 738.3632 | 69.0944 | -7.0977 | 76.1921 | 148.9396 | 100 | 7150 | 100 | 5175748 | 6.33 | 3969.08 | 58.8927 | -44928.26 | 302412.4 | VPC | 18.45% | 11.1% | -2.7197 | 29.1952 | N/A | 76.1921 | 1.2937 | 69.8705 | Water imported | Volume from own sources | Variable production cost (applied to Real Losses)
Lee County | GA1770068 | Lee | 14235 | 536.7769 | 0 | 0 | 536.7769 | 451.389 | 0 | 0 | 6.7097 | 458.0987 | 78.6782 | 18.842 | 59.8361 | 85.3879 | 85 | 5893 | 68 | 2355643 | 2.61 | 293.86 | 33.3531 | 49177.72 | 17583.44 | VPC | 15.91% | 2.918% | 8.7599 | 27.8185 | N/A | 59.8361 | 1.794 | 55.3444 | Volume from own sources | Customer metering inaccuracies | Customer retail unit cost (applied to Apparent Losses)
Leesburg | GA1770000 | Lee | 3266 | 154.795 | Note 1 | Note 1 | 143.3287 | 117.993 | Note 1 | 5.178 | 1.7916 | 124.9626 | 18.3661 | 1.8975 | 16.4686 | 25.3357 | 25.25 | 1866 | 62 | 418599 | 2.27 | 162.68 | Note 3 | 4307.22 | 37383.81 | CRUC | 17.68% | 13.74% | 2.7859 | 24.1798 | N/A | 16.4686 | Note 3 | 55.9815 | Volume from own sources | Unbilled metered | Customer retail unit cost (applied to Apparent Losses)
Lincoln County | GA1810038 | Lincoln | 5312 | 14.799 | 98.1273 | 0 | 116.0057 | 56.6702 | 0 | 0 | 1.4501 | 58.1202 | 57.8855 | 3.4143 | 54.4712 | 59.3356 | 128.6 | 2077 | 82 | 1158115.62 | 7.05 | 1991.68 | 30.1478 | 24071.02 | 108489.3 | VPC | 51.15% | 11.7% | 4.5038 | N/A | 1160.4668 | 54.4712 | 1.8068 | 59.4937 | Water imported | Customer metering inaccuracies | Billed metered
Locust Grove | GA1510002 | Henry | 5648 | 159.528 | 39.154 | 0 | 199.1776 | 161.833 | 0 | 0.178 | 2.4897 | 164.5007 | 34.6769 | 2.9533 | 31.7236 | 37.3446 | 43 | 2551 | 60 | 1642331 | 9.94 | 1714.47 | 13.4746 | 29355.79 | 54389.16 | VPC | 18.75% | 5.378% | 3.1718 | 34.0706 | N/A | 31.7236 | 2.3543 | 58.4023 | Volume from own sources | Unbilled metered | Customer metering inaccuracies
Loganville | GA1350006 | Walton | 10923 | 0 | 413.321 | Note 1 | 423.5714 | 313.807 | Note 1 | 50.111 | 5.2946 | 369.2126 | 54.3588 | 9.2703 | 45.0884 | 109.7644 | 81.4 | 5650 | 80 | 2943326 | 8.4 | 3.79 | 37.6059 | 77870.89 | 170.89 | VPC | 25.91% | 2.659% | 4.4953 | 21.8637 | N/A | 45.0884 | 1.199 | 73.1624 | Water imported | Customer metering inaccuracies | Customer retail unit cost (applied to Apparent Losses)
Louisville | GA1630002 | Jefferson | 3902 | 401.655 | 0 | 0 | 397.6782 | 321.568 | 0.576 | 19.628 | 4.971 | 346.743 | 50.9352 | 6.1171 | 44.8182 | 75.5342 | 40.3 | 1681 | 41 | 399994 | 2.55 | 385.64 | Note 3 | 15598.48 | 17283.69 | VPC | 18.99% | 10.59% | 9.9697 | 73.0455 | N/A | 44.8182 | Note 3 | 70.8719 | Customer metering inaccuracies | Unbilled metered | Billed metered
Lowndes County Utilities - North Lowndes | GA1850016 | Lowndes | 6430 | 580.547 | 0 | 0 | 580.547 | 267.8 | 0 | 0.33 | 7.2568 | 275.3868 | 305.1602 | 2.1209 | 303.0393 | 312.747 | 82 | 2932 | 61 | 472325 | 5.99 | 519.56 | 19.6693 | 12704 | 157447.1 | VPC | 53.87% | 36.86% | 1.9818 | 283.1667 | N/A | 303.0393 | 15.4067 | 68.1889 | Unbilled metered | Total annual cost of operating water system | Variable production cost (applied to Real Losses)
Lowndes County Utilities - South Lowndes | GA1850019 | Lowndes | 5879 | 301.773 | 0 | 0 | 301.773 | 247.7 | 0 | 5.325 | 3.7722 | 256.7972 | 44.9758 | 1.3737 | 43.6022 | 54.073 | 85 | 2724 | 61 | 436900 | 5.99 | 480.59 | 19.336 | 8228.36 | 20954.76 | VPC | 17.92% | 7.68% | 1.3816 | 43.8539 | N/A | 43.6022 | 2.255 | 68.9111 | Billed metered | Unbilled metered | Total annual cost of operating water system
Lyons | GA2790000 | Toombs | 4100 | 410.721 | 0 | 0 | 402.6676 | 325.994 | 0 | 14.881 | 5.0333 | 345.9083 | 56.7593 | 12.3642 | 44.3951 | 76.6736 | 42 | 2431 | 58 | 675497 | 2.1 | 835.18 | 12.5299 | 25964.78 | 37077.92 | VPC | 19.04% | 11.79% | 13.9344 | 50.0331 | N/A | 44.3951 | 3.5431 | 61.3922 | Volume from own sources | Variable production cost (applied to Real Losses) | Total annual cost of operating water system
Macon | GA0210001 | Bibb | 130024 | 8214.49 | 0 | 191.52 | 7530.11 | 5997.38 | 0 | 89.59 | 36.91 | 6123.88 | 1406.23 | 86.3619 | 1319.8681 | 1532.73 | 1394 | 54459 | 124.9 | 16321062 | 5.49 | 664.4 | 716.2131 | 474495.63 | 876920.37 | VPC | 20.35% | 8.795% | 4.3447 | 66.4 | N/A | 1319.8681 | 1.8428 | 78.0557 | Billed metered | Customer retail unit cost (applied to Apparent Losses) | Volume from own sources
Madison | GA2110002 | Morgan | 5215 | 455.307 | 0 | 19.883 | 421.8598 | 345.649 | 0 | 15.316 | 5.2732 | 366.2382 | 55.6216 | 11.1743 | 44.4473 | 76.2108 | 75 | 2880 | 60 | 3259736 | 6.3 | 533.92 | 18.3467 | 70398 | 23731.31 | VPC | 18.07% | 3.225% | 10.63 | 42.2824 | N/A | 44.4473 | 2.4226 | 71.3552 | Volume from own sources | Variable production cost (applied to Real Losses) | Customer retail unit cost (applied to Apparent Losses)
Manchester | GA1990003 | Meriwether | 4995 | 389.75 | 0 | 198.569 | 191.181 | 139.654 | Note 1 | 0.167 | 2.3898 | 142.2108 | 48.9702 | 16.1903 | 32.7799 | 51.527 | 113 | 2359 | 66 | 2181491.45 | 5.71 | 590.1 | 23.2512 | 92446.77 | 19343.43 | VPC | 26.95% | 5.194% | 18.8033 | N/A | 794.7608 | 32.7799 | 1.4098 | 60.0834 | Unbilled metered | Customer metering inaccuracies | Billed metered
Marietta | GA0670005 | Cobb | 60100 | 0 | 2710.139 | 0 | 2709.0554 | 2453.421 | 0.000438 | 0 | 33.8632 | 2487.2846 | 221.7707 | 18.5621 | 203.2087 | 255.6339 | 344.98 | 19339 | 86 | 19692485 | 7.52 | 3157.03 | 149.6422 | 139586.75 | 641535.9 | VPC | 9.436% | 4.509% | 2.6297 | 28.7883 | N/A | 203.2087 | 1.358 | 80.3081 | Water imported | Billed metered | Unauthorized consumption
Marion County | GA1970003 | Marion | 4558 | 316.4 | 0 | 0 | 316.4 | 92.632 | 0 | 0 | 3.955 | 96.587 | 219.813 | 1.0226 | 218.7904 | 223.768 | 360 | 4060 | 75 | 1105000 | 2 | 647.91 | 69.9869 | 2045.16 | 437580.84 | CRUC | 70.72% | 40.5% | 0.69005 | N/A | 1665.0717 | 218.7904 | 3.1262 | 38.4889 | Volume from own sources | Billed metered | Customer metering inaccuracies
McCaysville | GA1110001 | Fannin | 7020 | 316.34 | 1.896 | 30.282 | 288.2634 | 116.588 | Note 1 | 1.545 | 3.6033 | 121.7363 | 166.5271 | 2.2054 | 164.3217 | 171.6754 | 151 | 3450 | 89 | 1890468.42 | 7.52 | 999.1 | 43.3483 | 16584.54 | 164173.83 | VPC | 59.56% | 9.834% | 1.7514 | N/A | 2981.4337 | 164.3217 | 3.7907 | 67.1811 | Volume from own sources | Customer metering inaccuracies | Billed metered
McDonough | GA1510003 | Henry | 8962 | 411.71 | 0 | 0 | 416.1629 | 273.079 | 0 | 6.725 | 5.202 | 285.006 | 131.1569 | 2.2277 | 128.9292 | 143.0839 | 90 | 6200 | 74.4 | 2784435 | 4.68 | 543.47 | 38.4773 | 10425.45 | 70069.18 | VPC | 34.38% | 3.124% | 0.98438 | 56.9727 | N/A | 128.9292 | 3.3508 | 69.2363 | Volume from own sources | Unbilled metered | Customer metering inaccuracies
McRae-Helena | GA2710003 | Telfair | 5488 | 213.48 | 0 | 0 | 213.48 | 173.26 | 0 | 3.191 | 2.6685 | 179.1195 | 34.3605 | 6.8941 | 27.4664 | 40.22 | 39.8 | 1829 | 56 | 320115 | 2.43 | 181.07 | 10.0088 | 16752.77 | 4973.28 | VPC | 18.84% | 7.118% | 10.327 | 41.1429 | N/A | 27.4664 | 2.7442 | 50.9608 | Volume from own sources | Customer metering inaccuracies | Total annual cost of operating water system
Metter | GA0430000 | Candler | 4776 | 138.967 | 0 | 0 | 143.2649 | 129.97 | Note 1 | 1.684 | 1.7908 | 133.4448 | 9.8201 | 3.3699 | 6.4502 | 13.2949 | 58.4 | 2267 | 65 | 574472 | 3.87 | 263.81 | 15.5635 | 13041.53 | 1701.64 | VPC | 9.28% | 2.726% | 4.0726 | 7.7953 | N/A | 6.4502 | 0.41445 | 63.4334 | Volume from own sources | Billed metered | Unauthorized consumption
Milledgeville | GA0090001 | Baldwin | 19456 | 1985 | 0 | 0 | 1977.4856 | 800.702 | 218.951 | 2.89 | 610 | 1632.543 | 344.9426 | 15.0626 | 329.88 | 957.8326 | 250 | 7680 | 70 | 4258228 | 7.89 | 258.29 | 63.99 | 118843.6 | 85204.7 | VPC | 48.44% | 8.509% | 5.3733 | N/A | 3615.1232 | 329.88 | 5.1552 | 60.2148 | Volume from own sources | Billed unmetered | Unbilled metered
Millen | GA1650000 | Jenkins | 5879 | 170.226 | 0 | 0 | 175.4907 | 140.127 | 0 | 5.214 | 2.1936 | 147.5346 | 27.9561 | 6.8449 | 21.1112 | 35.3637 | 50 | 2020 | 60 | 178963 | 2.25 | 206.04 | 12.5597 | 15401.07 | 4349.75 | VPC | 20.15% | 11.89% | 9.2838 | 28.6331 | N/A | 21.1112 | 1.6809 | 48.0549 | Volume from own sources | Customer metering inaccuracies | Variable production cost (applied to Real Losses)
Monroe | GA2970001 | Walton | 21739 | 807.59 | 0 | 54.33 | 802.058 | 585.34 | 8.63 | Note 1 | 10.0257 | 603.9957 | 198.0623 | 7.8917 | 190.1706 | 208.088 | 218 | 10686 | 60 | 3261131.65 | 7.6 | 591.06 | 60.9319 | 59977.07 | 1445296.22 | CRUC | 25.94% | 48.49% | 2.0233 | 48.7568 | N/A | 190.1706 | 3.121 | 70.3039 | Volume from own sources | Variable production cost (applied to Real Losses) | Billed metered
Montezuma | GA1930002 | Macon | 4065 | 131.848 | 0 | 0 | 138.7874 | 73.31 | 0.288 | 0 | 5.35 | 78.948 | 59.8394 | 4.3887 | 55.4507 | 65.1894 | 38 | 1938 | 55 | 89877 | 4 | 682 | 9.9628 | 17554.66 | 37817.38 | VPC | 46.97% | 65.67% | 6.2042 | 78.39 | N/A | 55.4507 | 5.5658 | 56.098 | Volume from own sources | Billed metered | Billed unmetered
Monticello | GA1590000 | Jasper | 3505 | 154.36 | 0 | 0 | 151.3333 | 104.56 | Note 1 | 19.774 | 1.8917 | 126.2257 | 25.1077 | 7.1836 | 17.924 | 46.7733 | 29.5 | 2081 | 65 | 601944.63 | 5.14 | 747.36 | 11.1922 | 36923.85 | 13395.71 | VPC | 30.91% | 11.05% | 9.4576 | 23.5978 | N/A | 17.924 | 1.6015 | 45.098 | Volume from own sources | Customer metering inaccuracies | Customer retail unit cost (applied to Apparent Losses)
Moultrie | GA0710004/GA0710021 | Colquitt | 14361 | 930.83 | 0 | 0 | 921.6139 | 662.292 | 0 | 17.989 | 39.68 | 719.961 | 201.6529 | 17.8431 | 183.8098 | 259.3219 | 219.89 | 7323 | 65 | 1396797 | 2.4 | 189.58 | 54.2841 | 42823.32 | 34846.66 | VPC | 28.14% | 6.343% | 6.6756 | 68.7681 | N/A | 183.8098 | 3.3861 | 66.8026 | Volume from own sources | Customer metering inaccuracies | Variable production cost (applied to Real Losses)
Nashville | GA0190002 | Berrien | 4680 | 185.051 | 0 | 0 | 228.458 | 161.375 | Note 1 | 3.269 | 2.8557 | 167.4997 | 60.9583 | 9.6401 | 51.3182 | 67.083 | 85 | 2300 | 60 | 575000 | 2.95 | 0.29 | 17.6262 | 28438.17 | 14.88 | VPC | 29.36% | 4.949% | 11.4831 | N/A | 1654.0933 | 51.3182 | 2.9115 | 44.0196 | Volume from own sources | Total annual cost of operating water system | Customer retail unit cost (applied to Apparent Losses)
Newnan | GA0770002 | Coweta | 34000 | 2511.16 | 53.37 | 1148.275 | 1415.2034 | 1082.917 | 0 | 65.182 | 17.69 | 1165.789 | 249.4144 | 6.2453 | 243.1691 | 332.2864 | 259.9 | 19976 | 85 | 11031139 | 7.35 | 462.42 | 136.5863 | 45902.96 | 112446.24 | VPC | 23.48% | 1.783% | 0.85655 | 33.3509 | N/A | 243.1691 | 1.7803 | 73.5686 | Volume from own sources | Customer metering inaccuracies | Variable production cost (applied to Real Losses)
Newton County | GA2170097 | Newton | 60635 | 0 | 5863.846 | 3989.066 | 2100.1149 | 1724.916 | Note 1 | 3.147 | 26.2514 | 1754.3144 | 345.8005 | 35.8783 | 309.9222 | 375.1989 | 636.52 | 30847 | 107.8 | 7714187.15 | 7.67 | 2260 | 317.5548 | 275186.24 | 700424.24 | VPC | 17.87% | 13.51% | 3.1866 | 27.5262 | N/A | 309.9222 | 0.97596 | 73.0005 | Water imported | Water exported | Billed metered
North Fulton County | GA1210005 | Fulton | 172533 | 0 | 9602.131 | 5.011 | 9591.3597 | 8676.9335 | Note 1 | 19 | 119.892 | 8815.8255 | 775.5341 | 167.3538 | 608.1803 | 914.4261 | 1524 | 78619 | 97.88 | 23658041 | 3.59 | 693.57 | 715.8705 | 600800.3 | 421815.6 | VPC | 9.534% | 4.73% | 5.832 | 21.194 | N/A | 608.1803 | 0.84957 | 67.5742 | Water imported | Unbilled metered | Variable production cost (applied to Real Losses)
Notla Water Authority | GA2910003 | Union | 13465 | 294.644 | 0 | 0 | 294.644 | 216.108 | Note 1 | 4.674 | 14.674 | 235.456 | 59.188 | 1.2769 | 57.9111 | 78.536 | 533 | 6629 | 90 | 2226262 | 9.06 | 498.22 | 127.3884 | 11568.53 | 28852.48 | VPC | 26.65% | 2.249% | 0.52773 | N/A | 297.6747 | 57.9111 | 0.4546 | 67.7157 | Volume from own sources | Billed metered | Customer metering inaccuracies
Oconee County-Watkinsville | GA2190000 | Oconee | 21897 | 13.905 | 880.44 | 11.205 | 929.5914 | 778.484 | 0 | 0 | 1.1 | 779.584 | 150.0074 | 12.2565 | 137.751 | 151.1074 | 301 | 13100 | 68 | 3866610.36 | 8.63 | 1646.73 | 89.1884 | 105773.19 | 226838.69 | VPC | 16.26% | 8.649% | 2.5633 | 28.8092 | N/A | 137.751 | 1.5445 | 54.3642 | Water imported | Billed metered | Unauthorized consumption
Oglethorpe | GA1930003 | Macon | 4048 | 203.972 | 0 | 0 | 208.1347 | 119.847 | 0 | 0.643 | 2.6017 | 123.0917 | 85.043 | 2.6548 | 82.3882 | 88.2877 | 48 | 1456 | 60 | 364955.74 | 1.75 | 208.22 | Note 3 | 4645.95 | 17154.87 | VPC | 42.42% | 6.159% | 4.9955 | N/A | 4702.5219 | 82.3882 | Note 3 | 67.6765 | Volume from own sources | Total annual cost of operating water system | Customer metering inaccuracies
Palmetto | GA1210008 | Fulton | 3965 | 128.24 | 10.685 | 0 | 137.6553 | 100.883 | 0 | 0.491 | 1.7207 | 103.0947 | 34.5606 | 3.1957 | 31.3649 | 36.7723 | 34.5 | 1651 | 55 | 756428.61 | 4.54 | 259.6 | Note 3 | 14508.38 | 8142.34 | VPC | 26.71% | 3.07% | 5.303 | 52.048 | N/A | 31.3649 | Note 3 | 58.6347 | Volume from own sources | Billed metered | Customer metering inaccuracies
Paulding County | GA2230002 | Paulding | 117468 | 0 | 4299.148 | 258.202 | 4040.5085 | 2894.76 | 0 | 0 | 50.5064 | 2945.2664 | 1095.2421 | 137.9532 | 957.289 | 1145.7485 | 986 | 54976 | 99.5 | 35272950.47 | 7.94 | 3240 | 493.2156 | 1095348.18 | 7600874.47 | CRUC | 28.36% | 25.79% | 6.8749 | 47.7064 | N/A | 957.289 | 1.9409 | 83.0904 | Water imported | Unauthorized consumption | Systematic data handling errors
Pelham | GA2050003 | Mitchell | 3414 | 209.618 | 0 | 115.043 | 131.432 | 102.144 | Note 1 | 1.359 | 1.6429 | 105.1459 | 26.2861 | 4.8966 | 21.3895 | 29.288 | 47 | 2146 | 62 | 205174 | 2.3 | 320.87 | 13.0387 | 11262.1 | 6863.26 | VPC | 22.28% | 9.304% | 6.2513 | 27.3073 | N/A | 21.3895 | 1.6405 | 67.6805 | Volume from own sources | Variable production cost (applied to Real Losses) | Water exported
Perry | GA1530006 | Houston | 14267 | 677.482 | 0 | 0 | 678.8397 | 514.486 | 0.006 | Note 1 | 8.4855 | 522.9775 | 155.8622 | 8.1801 | 147.682 | 164.3477 | 149 | 8561 | 50 | 675900 | 3.54 | 280.24 | 38.1469 | 28957.7 | 41386.42 | VPC | 24.21% | 10.76% | 2.6178 | 47.2618 | N/A | 147.682 | 3.8714 | 63.0897 | Volume from own sources | Billed metered | Customer metering inaccuracies
Pickens County Water | GA2270002 | Pickens | 6357 | 0 | 258.6517 | 42.019 | 216.6327 | 171.7258 | 0 | 0.14087 | 2.7079 | 174.5746 | 42.0581 | 4.4784 | 37.5797 | 44.9069 | 142.9 | 3382 | 110 | 2184714.22 | 5.16 | 2444.81 | 51.4076 | 23108.44 | 91875.33 | VPC | 20.73% | 5.582% | 3.6279 | N/A | 720.4912 | 37.5797 | 0.73102 | 64.9118 | Water imported | Customer metering inaccuracies | Customer retail unit cost (applied to Apparent Losses)
Polk County Water Authority | GA2330001 | Polk | 23325 | 893.09 | 5.7578 | 7.297 | 891.4379 | 527.9431 | 0 | 8.176 | 11.143 | 547.262 | 344.1759 | 14.4897 | 329.6862 | 363.4949 | 500 | 9573 | 97 | 3784341.58 | 7.33 | 477.29 | 146.6103 | 106209.19 | 157355.94 | VPC | 40.78% | 7.208% | 4.1468 | N/A | 1806.4999 | 329.6862 | 2.2487 | 64.5602 | Volume from own sources | Customer metering inaccuracies | Billed metered
Pooler | GA0510001 | Chatham | 21187 | 420.347 | 362.316 | 3.179 | 818.031 | 683.143 | 0 | 2.38 | 10.2254 | 695.7484 | 122.2826 | 21.3304 | 100.9522 | 134.888 | 107.5 | 10358 | 61 | 2039222 | 8.48 | 2492.84 | 47.5419 | 180882.2 | 251657.65 | VPC | 16.49% | 22.75% | 5.642 | 26.7022 | N/A | 100.9522 | 2.1234 | 66.6337 | Billed metered | Variable production cost (applied to Real Losses) | Customer metering inaccuracies
Port Wentworth | GA0210002 | Chatham | 5500 | 10.9561 | 330.0716 | 0 | 347.2715 | 162.965 | 0 | 169.537 | 4.3409 | 336.8429 | 10.4287 | 1.2756 | 9.1531 | 184.3066 | 59 | 4030 | 62 | 843250 | 2.82 | 1493.44 | 20.9031 | 3598.01 | 13669.6 | VPC | 53.07% | 32.84% | 0.86719 | 6.2226 | N/A | 9.1531 | 0.43788 | 50.4378 | Water imported | Customer metering inaccuracies | Variable production cost (applied to Real Losses)
Powder Springs | GA0670006 | Cobb | 14000 | 0 | 498.177 | 0 | 495.6985 | 366.356 | 0 | 0.196 | 6.1962 | 372.7482 | 122.9503 | 9.6358 | 113.3145 | 129.3425 | 97 | 7513 | 125 | 4337383 | 7.68 | 2926.52 | 75.3597 | 74002.86 | 870255.26 | CRUC | 26.09% | 22.9% | 3.5138 | 41.3218 | N/A | 113.3145 | 1.5036 | 79.6068 | Water imported | Billed metered | Customer metering inaccuracies
Quitman | GA0270002 | Brooks | 4942 | 460.773 | 0 | 0 | 438.8314 | 165.33 | 0 | 0 | 5.4854 | 170.8154 | 268.016 | 1.5104 | 266.5056 | 273.5014 | 50 | 2741 | 57 | 366003.02 | 3.52 | 151 | 14.1817 | 5316.62 | 40242.35 | VPC | 62.32% | 12.67% | 1.5097 | 266.3818 | N/A | 266.5056 | 18.7922 | 50.3444 | Volume from own sources | Customer metering inaccuracies | Unauthorized consumption
Reynolds Water System | GA1330046 | Greene | 7062 | 278.0053 | 0 | 0 | 274.5731 | 234.9011 | 0 | 0.7 | 3.4322 | 239.0332 | 35.5399 | 11.0904 | 24.4495 | 39.672 | 172.5 | 3845 | 75 | 1204595 | 11.92 | 689.49 | 41.3356 | 132197.53 | 16857.67 | VPC | 14.45% | 12.61% | 7.9024 | N/A | 388.3181 | 24.4495 | 0.59149 | 65.3076 | Volume from own sources | Customer metering inaccuracies | Unbilled metered
Richmond Hill | GA0290000 | Bryan | 12594 | 485.93 | 0 | 0 | 485.5416 | 442.795 | 0 | 1.42 | 6.0693 | 450.2843 | 35.2573 | 6.8079 | 28.4494 | 42.7466 | 90 | 6501 | 52 | 262500 | 3.4 | 540.63 | 27.7497 | 23146.73 | 15380.62 | VPC | 8.804% | 16.22% | 2.869 | 11.9895 | N/A | 28.4494 | 1.0252 | 69.5322 | Volume from own sources | Unbilled metered | Customer metering inaccuracies
Rincon | GA1030001 | Effingham | 9880 | 345.279 | 0.017 | 0 | 345.296 | 601.591 | 0 | 57.599 | 4.3162 | 663.5062 | -318.2102 | 2.3672 | -320.5774 | -256.295 | 1381.5 | 4942 | 65 | 476645 | 4.5 | 98543.63 | 194.906 | 10652.48 | -31590862.42 | VPC | -74.22% | -5345% | 1.3123 | N/A | -635.7541 | -320.5774 | -1.6448 | 67 | Volume from own sources | Customer metering inaccuracies | Customer retail unit cost (applied to Apparent Losses)
Ringgold | GA0470002 | Catoosa | 3584 | 113.45 | 27 | 0 | 138.7973 | 125.15 | 0 | 6.875 | 1.735 | 133.76 | 5.0374 | 0.79203 | 4.2453 | 13.6473 | 28 | 1300 | 99.8 | 460157.56 | 4.6 | 303.22 | Note 3 | 3643.32 | 19528.51 | CRUC | 9.833% | 13.64% | 1.6692 | 8.947 | N/A | 4.2453 | Note 3 | 64.3094 | Volume from own sources | Unbilled metered | Water imported
Rockdale County | GA2470000 | Rockdale | 72621 | 4099.5 | 0 | 0 | 4140.9091 | 2739.551 | 0 | 30.42 | 51.7614 | 2821.7324 | 1319.1767 | 45.1807 | 1273.9961 | 1401.3581 | 648.84 | 28129 | 80 | 7252698 | 4.07 | 1715.08 | 225.7036 | 183885.27 | 2185005.18 | VPC | 33.84% | 34.61% | 4.4005 | 124.0855 | N/A | 1273.9961 | 5.6446 | 67.6947 | Volume from own sources | Variable production cost (applied to Real Losses) | Billed metered
Rockmart | GA2330002 | Polk | 6500 | 566.57 | 0 | 0 | 566.3435 | 383.486 | 0 | 4.278 | 7.0793 | 394.8433 | 171.5002 | 14.3673 | 157.1329 | 182.8575 | 67.5 | 3404 | 60 | 1478051 | 5.62 | 319.85 | 19.1795 | 80744.08 | 50258.96 | VPC | 32.29% | 9.109% | 11.5636 | 126.4692 | N/A | 157.1329 | 8.1928 | 62.4608 | Customer metering inaccuracies | Variable production cost (applied to Real Losses) | Billed metered
Rome | GA1150002 | Floyd | 45586 | 2441 | 0 | 243 | 2198 | 1644 | 2.4 | 183 | 50.1 | 1879.5 | 318.5 | 113.11 | 205.39 | 551.6 | 291 | 18602 | 85 | 4331940 | 3.48 | 460 | 135.412 | 393135.8 | 94479.4 | VPC | 25.1% | 13.73% | 16.659 | 30.2501 | N/A | 205.39 | 1.5168 | 78.6568 | Volume from own sources | Systematic data handling errors | Customer retail unit cost (applied to Apparent Losses)
Roswell | GA1210009 | Fulton | 14300 | 556.302 | 4.199 | 0 | 561.1052 | 495.1 | 0 | 10.325 | 0.321 | 505.746 | 55.3592 | 10.8028 | 44.5565 | 66.0052 | 87.9 | 5601 | 89 | 4573615.6 | 8.42 | 490.79 | 42.7402 | 90959.27 | 21867.88 | VPC | 11.76% | 2.581% | 5.2842 | 21.7948 | N/A | 44.5565 | 1.0425 | 82.6107 | Volume from own sources | Unauthorized consumption | Customer metering inaccuracies
Sandersville | GA3030005 | Washington | 7904 | 760.66 | 0 | 84.904 | 670.9173 | 435.758 | Note 1 | 6.748 | 8.3865 | 450.8925 | 220.0248 | 2.8906 | 217.1342 | 235.1593 | 70.3 | 3107 | 61.9 | 1358333 | 1.9 | 357.53 | 19.1225 | 5492.19 | 77631.98 | VPC | 35.05% | 6.518% | 2.5489 | 191.4671 | N/A | 217.1342 | 11.3549 | 72.9067 | Volume from own sources | Customer retail unit cost (applied to Apparent Losses) | Unauthorized consumption
Satilla Regional Water & Sewer Authority | GA2990051/GA2990001 | Ware | 10657 | 374.609 | 0 | 0 | 378.3929 | 352.098 | 0 | 0 | 4.7299 | 356.8279 | 21.565 | 3.5956 | 17.9695 | 26.2949 | 234.5 | 6654 | 51 | 1437721 | 2.8 | 253.63 | 42.1955 | 10067.58 | 4557.59 | VPC | 6.949% | 1.101% | 1.4804 | N/A | 209.9419 | 17.9695 | 0.42586 | 80.9 | Customer retail unit cost (applied to Apparent Losses) | Volume from own sources | Unauthorized consumption
Savannah - Georgetown Gateway | GA0510081 | Chatham | 13589 | 630.456 | 0 | 0 | 649.9546 | 488.91 | 0 | 6.91 | 8.1244 | 503.9444 | 146.0102 | 25.1795 | 120.8307 | 161.0446 | 101 | 6019 | 57.5 | 2219849 | 3.44 | 193.34 | 30.4163 | 86506.54 | 23361.4 | VPC | 24.78% | 5.08% | 11.4612 | 54.9997 | N/A | 120.8307 | 3.9726 | 53.6196 | Volume from own sources | Billed metered | Variable production cost (applied to Real Losses)
Savannah - Savannah Main | GA0510003 | Chatham | 168958 | 6307.0131 | 0 | 45.7239 | 6456.1862 | 5081.15 | 0 | 263.79 | 80.7023 | 5425.6423 | 1030.5439 | 269.5863 | 760.9576 | 1375.0362 | 677 | 57053 | 52 | 20230160 | 1.68 | 163.82 | 231.9455 | 452904.94 | 124660.07 | VPC | 21.3% | 3.134% | 12.9457 | 36.5417 | N/A | 760.9576 | 3.2808 | 54.3856 | Volume from own sources | Billed metered | Variable production cost (applied to Real Losses)
Savannah - Savannah Quarters | GA0510259 | Chatham | 3530 | 90.1234 | 0 | 1.187 | 89.8468 | 82.92 | 0 | 3.5 | 1.1231 | 87.5431 | 2.3037 | 2.1956 | 0.1081 | 6.9268 | 18 | 1066 | 53.7 | 339362 | 3.45 | 390.81 | Note 3 | 7572.5 | 42.25 | VPC | 7.71% | 2.776% | 5.6429 | 0.27782 | N/A | 0.1081 | Note 3 | 55.6746 | Volume from own sources | Variable production cost (applied to Real Losses) | Billed metered
Savannah - Whitemarsh | GA0510250 | Chatham | 4247 | 234.9378 | 0 | 0 | 242.2039 | 176.52 | 0 | 0.37 | 3.0275 | 179.9175 | 62.2863 | 9.0142 | 53.2722 | 65.6839 | 24.3 | 1707 | 62.9 | 748325.61 | 3.22 | 156.34 | Note 3 | 29040.94 | 8328.57 | VPC | 27.12% | 5.065% | 14.4677 | 85.5016 | N/A | 53.2722 | Note 3 | 54.3844 | Volume from own sources | Billed metered | Variable production cost (applied to Real Losses)
Savannah - Wilmington | GA0510229 | Chatham | 13526 | 496.4917 | 0 | 0 | 511.8471 | 378 | 0 | 0.62 | 6.3981 | 385.0181 | 126.8291 | 9.9516 | 116.8775 | 133.8471 | 56.71 | 5223 | 55.7 | 1612839 | 3.54 | 128.22 | 22.1653 | 35253.74 | 14986.03 | VPC | 26.15% | 3.171% | 5.2201 | 61.3081 | N/A | 116.8775 | 5.273 | 55.404 | Volume from own sources | Variable production cost (applied to Real Losses) | Billed metered
Senoia | GA0770003 | Coweta | 3466 | 144.019 | 16.899 | 0 | 141.7096 | 129.322 | 0.023 | 0.179 | 1.7714 | 131.2954 | 10.4143 | 8.9436 | 1.4707 | 12.3646 | 55 | 2370 | 60 | 1236900 | 0.91 | 96.94 | 14.3018 | 8138.68 | 142.57 | VPC | 8.725% | 0.6848% | 10.3388 | 1.7001 | N/A | 1.4707 | 0.10283 | 44.4771 | Volume from own sources | Variable production cost (applied to Real Losses) | Unbilled metered
Smyrna | GA0670007 | Cobb | 35000 | 0 | 1426.592 | 0 | 1428.449 | 1252.205 | 0 | 15.461 | 17.8556 | 1285.5216 | 142.9274 | 29.4123 | 113.5151 | 176.244 | 200.5 | 15625 | 106 | 10846444.38 | 5.09 | 3088.62 | 132.6469 | 149708.42 | 350605.03 | VPC | 12.34% | 5.561% | 5.1572 | 19.904 | N/A | 113.5151 | 0.85577 | 78.7525 | Water imported | Customer metering inaccuracies | Unauthorized consumption
Social Circle | GA2970002 | Walton | 4235 | 193.16 | 10.35 | 0 | 203.51 | 161.99 | 0 | 6.18 | 2.5439 | 170.7139 | 32.7961 | 6.1149 | 26.6812 | 41.52 | 24.5 | 2267 | 65 | 1685838.62 | 6.83 | 494.34 | 11.2123 | 41764.66 | 13189.6 | VPC | 20.4% | 3.516% | 7.39 | 32.2449 | N/A | 26.6812 | 2.3796 | 59.5588 | Volume from own sources | Customer metering inaccuracies | Customer retail unit cost (applied to Apparent Losses)
South Atlantic Utilities (Bryan County) | GA0290080 | Bryan | 3234 | 137.939 | 0 | 0 | 172.4237 | 151.161 | 0 | 0 | 12.07 | 163.231 | 9.1927 | 2.3358 | 6.8569 | 21.2627 | 12 | 1333 | 45 | 521367 | 4 | 335.37 | Note 3 | 9343.36 | 2299.6 | VPC | 12.33% | 3.01% | 4.8009 | 14.0931 | N/A | 6.8569 | Note 3 | 73.0333 | Volume from own sources | Master meter error adjustment | Billed metered
South Monroe County Water System | GA2070074 | Monroe | 5370 | 0 | 201.914 | 0 | 210.3271 | 165.651 | 0 | 2.168 | 2.6291 | 170.4481 | 39.879 | 4.3648 | 35.5142 | 44.6761 | 72 | 3859 | 63 | 1737672 | 5.56 | 2223.01 | 22.2677 | 24268.41 | 78948.36 | VPC | 21.24% | 6.554% | 3.0988 | 25.2136 | N/A | 35.5142 | 1.5949 | 75.8929 | Water imported | Customer metering inaccuracies | Billed metered
Spalding County | GA2550036 | Spalding | 40430 | 0 | 955.7345 | 0 | 955.7345 | 773.756 | 0 | 34.3393 | 11.9467 | 820.042 | 135.6925 | 16.6297 | 119.0627 | 181.9785 | 523 | 13555 | 97 | 394814.99 | 8.07 | Note 2 & B | 191.9324 | 134202.05 | Note 4 | VPC | 19.04% | 33.99% | 3.3612 | N/A | 623.7079 | 119.0627 | 0.62034 | 52.4412 | Water imported | Unauthorized consumption | Systematic data handling errors
Sparta | GA1410001 | Hancock | 3710 | 335.7 | 0 | 36.021 | 292.6632 | 164.527 | 0 | 0 | 3.6583 | 168.1853 | 124.4779 | 2.8049 | 121.6731 | 128.1362 | 53 | 2029 | 59 | 1082525 | 3.29 | 1195.33 | 12.7289 | 9228 | 145439.48 | VPC | 43.78% | 14.69% | 3.7874 | 164.2932 | N/A | 121.6731 | 9.5588 | 47.7449 | Volume from own sources | Billed metered | Customer metering inaccuracies
St. Marys | GA0390001 | Camden | 17270 | 500.406 | 0 | 0 | 485.8311 | 437.551 | Note 1 | 2.514 | 6.0729 | 446.1379 | 39.6932 | 23.0445 | 16.6487 | 48.2801 | 130 | 6903 | 53 | 1284319.2 | 5.14 | 227.09 | 33.6361 | 118448.74 | 85574.2 | CRUC | 9.938% | 19.32% | 9.1461 | 6.6077 | N/A | 16.6487 | 0.49496 | 75.1393 | Customer retail unit cost (applied to Apparent Losses) | Variable production cost (applied to Real Losses) | Volume from own sources
Statesboro | GA0310004 | Bulloch | 36846 | 1175.845 | 0 | 0 | 1175.845 | 1056.165 | Note 1 | Note 1 | 14.6981 | 1070.8631 | 104.9819 | 16.2484 | 88.7336 | 119.68 | 245.47 | 14055 | 62.3 | 2278983.22 | 4.55 | 262.79 | 78.1384 | 73930.03 | 23318.3 | VPC | 10.18% | 4.437% | 3.1673 | 17.2967 | N/A | 88.7336 | 1.1356 | 65.7 | Volume from own sources | Customer metering inaccuracies | Variable production cost (applied to Real Losses)
Statham | GA0130001 | Barrow | 3986 | 76.56 | 35.1375 | 0 | 112.1243 | 75.808 | 0 | 0.17969 | 1.4016 | 77.3892 | 34.735 | 2.82 | 31.9151 | 36.3163 | 38 | 1753 | 83 | 499862.41 | 10.54 | 1838.33 | Note 3 | 29722.43 | 58670.42 | VPC | 32.39% | 18.26% | 4.4073 | 49.8794 | N/A | 31.9151 | Note 3 | 58.3631 | Volume from own sources | Unbilled metered | Customer metering inaccuracies
Stockbridge | GA1510004 | Henry | 6500 | 110.852 | 202.5 | 0 | 322.318 | 211.0201 | 0 | 10.09 | 4.029 | 225.1391 | 97.1789 | 5.8458 | 91.3331 | 111.2979 | 47 | 2710 | 88.6 | 2154983.6 | 8.97 | 2155.42 | 21.3686 | 52436.79 | 196861.27 | VPC | 34.53% | 12.98% | 5.9099 | 92.335 | N/A | 91.3331 | 4.2742 | 73.8156 | Unbilled metered | Volume from own sources | Unauthorized consumption
Summerville | GA0550003 | Chattooga | 11651 | 687.141 | 0 | 0.239 | 663.6689 | 509.14 | Note 1 | 3.6 | 8.2959 | 521.0359 | 142.633 | 10.7402 | 131.8928 | 154.5289 | 225 | 5573 | 80 | 3057404.84 | 3.73 | 481.26 | 59.9534 | 40061.12 | 491960.04 | CRUC | 23.28% | 18.85% | 5.28 | N/A | 1606.0003 | 131.8928 | 2.1999 | 62.9508 | Volume from own sources | Customer retail unit cost (applied to Apparent Losses) | Variable production cost (applied to Real Losses)
Swainsboro | GA1070005 | Emanuel | 8500 | 398.5513 | 0 | 0 | 400.6313 | 327.588 | 0 | 2.3671 | 5.0079 | 334.963 | 65.6683 | 5.4637 | 60.2046 | 73.0433 | 60 | 3093 | 55 | 919299 | 2.32 | 276.59 | 15.8301 | 12678.7 | 16652.15 | VPC | 18.23% | 3.412% | 4.8396 | 53.3282 | N/A | 60.2046 | 3.8032 | 61.4106 | Billed metered | Volume from own sources | Customer metering inaccuracies
Sylvania | GA2510003 | Screven | 4910 | 266.871 | 0 | 0 | 270.1123 | 142.983 | Note 1 | Note 1 | 3.3764 | 146.3594 | 123.7529 | 8.5582 | 115.1948 | 127.1293 | 127 | 1430 | 60 | 426278.2 | 4.02 | 293.34 | 19.7444 | 34403.8 | 33791.24 | VPC | 47.07% | 16.23% | 16.3965 | N/A | 2485.0563 | 115.1948 | 5.8343 | 35.6866 | Volume from own sources | Customer metering inaccuracies | Variable production cost (applied to Real Losses)
Sylvester | GA3210003 | Worth | 6443 | 371.32 | 0 | 0 | 360.5049 | 203.231 | Note 1 | Note 1 | 4.5063 | 207.7373 | 152.7675 | 10.9857 | 141.7819 | 157.2739 | 82 | 3080 | 80 | 99000 | 4.77 | 140.58 | 26.4441 | 52401.64 | 676299.54 | CRUC | 43.63% | 757.8% | 9.772 | 126.118 | N/A | 141.7819 | 5.3616 | 73.185 | Customer retail unit cost (applied to Apparent Losses) | Variable production cost (applied to Real Losses) | Billed metered
Talbot County | GA2630005 | Talbot | 3369 | 0 | 165.37 | 36.7817 | 128.5883 | 69.1321 | 0 | 3.207 | 1.6074 | 73.9465 | 54.6418 | 4.3016 | 50.3402 | 59.4561 | 150 | 1682 | 70 | 906385.87 | 10.34 | 2134.27 | 27.1801 | 44478.8 | 107439.48 | VPC | 46.24% | 17.89% | 7.0067 | N/A | 919.4548 | 50.3402 | 1.8521 | 53.442 | Water imported | Customer metering inaccuracies | Water exported
Tallapoosa | GA1430002 | Haralson | 4030 | 0 | 201.091 | 0 | 198.7851 | 142.157 | 0 | 0 | 2.4848 | 144.6418 | 54.1433 | 3.7535 | 50.3898 | 56.6281 | 31 | 1736 | 80 | 900565.06 | 8.72 | 2610 | Note 3 | 32730.68 | 131517.28 | VPC | 28.49% | 18.96% | 5.9237 | 79.5243 | N/A | 50.3898 | Note 3 | 80.2191 | Customer metering inaccuracies | Unauthorized consumption | Systematic data handling errors
Temple | GA0450005 | Carroll | 4500 | 0 | 125.9 | 0 | 125.9 | 105.5 | 0 | 2.16 | 1.5738 | 109.2338 | 16.6663 | 4.4833 | 12.183 | 20.4 | 44 | 2699 | 50 | 754433 | 4.5 | 2170 | 11.7327 | 20174.7 | 26437.07 | VPC | 16.2% | 7.252% | 4.5509 | 12.3668 | N/A | 12.183 | 1.0384 | 54.0686 | Water imported | Unbilled metered | Customer metering inaccuracies
The Landings Subdivision | GA0510033 | Chatham | 11058 | 509.596 | 0 | 0 | 506.883 | 449.953 | 0 | 0.223 | 1.329 | 451.505 | 55.378 | 9.2476 | 46.1304 | 56.93 | 95.4 | 4706 | 56.9 | 816616 | 4.3 | 370.49 | 25.3794 | 39764.52 | 198360.88 | CRUC | 11.23% | 29.98% | 5.3837 | 26.8561 | N/A | 46.1304 | 1.8176 | 78.8877 | Volume from own sources | Variable production cost (applied to Real Losses) | Unauthorized consumption
Thomaston | GA2930000 | Upson | 12482 | 589.42 | 0 | 25.067 | 564.353 | 367.142 | Note 1 | 28.778 | 7.0544 | 402.9744 | 161.3786 | 14.5737 | 146.8049 | 197.211 | 114 | 4758 | 80 | 2993557 | 7.11 | 610.26 | 38.8488 | 103618.91 | 89589.16 | VPC | 34.94% | 7.185% | 8.3917 | 84.5324 | N/A | 146.8049 | 3.7789 | 62.3223 | Volume from own sources | Customer metering inaccuracies | Billed metered
Thomasville | GA2750005 | Thomas | 24206 | 1657.474 | 0 | 0 | 1632.9793 | 1203.411 | Note 1 | 1.9 | 20.4122 | 1225.7232 | 407.2561 | 31.6892 | 375.5669 | 429.5683 | 268.4 | 14359 | 66.4 | 5790848.02 | 4.1 | 3.57 | 87.3924 | 129925.55 | 1340.77 | VPC | 26.31% | 2.268% | 6.0464 | 71.6589 | N/A | 375.5669 | 4.2975 | 77.3235 | Volume from own sources | Billed metered | Unauthorized consumption
Thomson-McDuffie County | GA1890001 | Mcduffie | 17717 | 727.39 | 0 | 0 | 720.1881 | 574.573 | 0 | 0 | 28.5 | 603.073 | 117.1151 | 14.9629 | 102.1522 | 145.6151 | 278.5 | 7675 | 62 | 3099026 | 4.41 | 635.8 | 60.1491 | 65986.31 | 64948.39 | VPC | 20.22% | 4.81% | 5.3413 | N/A | 1004.9161 | 102.1522 | 1.6983 | 55.1627 | Volume from own sources | Billed metered | Customer metering inaccuracies
Tifton-Tift County Water System | GA2770001 | Tift | 26452 | 1623.159 | 0 | 0.002 | 1623.157 | 1346.389 | 0 | 0 | 20.2895 | 1366.6785 | 256.4785 | 39.1198 | 217.3587 | 276.768 | 285 | 11820 | 61.3 | 3563200 | 1.45 | 236.39 | 74.1681 | 56723.74 | 51381.43 | VPC | 17.05% | 3.169% | 9.0675 | 50.381 | N/A | 217.3587 | 2.9306 | 54.8445 | Volume from own sources | Variable production cost (applied to Real Losses) | Billed metered
Toccoa | GA2570001 | Stephens | 24960 | 1154.64 | 0 | 147.78 | 1325.0047 | 666.81 | 0 | 103.89 | 60.02 | 830.72 | 494.2847 | 27.1808 | 467.1039 | 658.1947 | 613.5 | 10984 | 125 | 4685373 | 6.84 | 336.59 | 226.6027 | 185916.48 | 157222.5 | VPC | 49.67% | 8.501% | 6.7797 | N/A | 2085.9603 | 467.1039 | 2.0613 | 59.8943 | Volume from own sources | Master meter error adjustment | Customer metering inaccuracies
Towns County Water and Sewerage Authority | GA2810007 | Towns | 9991 | 0 | 212.497 | 0 | 213.3933 | 132.615 | 0 | 0.031 | 4.627 | 137.273 | 76.1203 | 1.206 | 74.9142 | 80.7783 | 204 | 4319 | 100 | 1870615.75 | 5.09 | 1958.15 | 63.9294 | 6138.65 | 146693.3 | VPC | 37.85% | 8.658% | 0.76503 | N/A | 1006.1003 | 74.9142 | 1.1718 | 74.5492 | Billed metered | Customer metering inaccuracies | Water imported
Tybee Island Water & Sewer Department | GA0510005 | Chatham | 8047 | 273.774 | 0 | 0 | 280.7938 | 253.844 | 0 | 0.974 | 3.5099 | 258.3279 | 22.4659 | 2.6171 | 19.8488 | 26.9498 | 33.9 | 3406 | 62.3 | 783324 | 3.93 | 113.52 | 15.788 | 10285.15 | 2253.24 | VPC | 9.598% | 1.666% | 2.1051 | 15.9661 | N/A | 19.8488 | 1.2572 | 73.2872 | Volume from own sources | Variable production cost (applied to Real Losses) | Unauthorized consumption
Unadilla | GA0930003 | Dooly | 3522 | 207.489 | 0 | 0 | 207.489 | 142.132 | Note 1 | 0.056 | 2.5936 | 144.7816 | 62.7074 | 0.87405 | 61.8333 | 65.357 | 35.1 | 868 | 65 | 296552.96 | 4 | 132.51 | Note 3 | 3496.21 | 8193.54 | VPC | 31.5% | 4.06% | 2.7588 | N/A | 4826.3931 | 61.8333 | Note 3 | 62.7941 | Volume from own sources | Unbilled metered | Variable production cost (applied to Real Losses)
Union City | GA1210010 | Fulton | 18636 | 0 | 505.807 | Note 1 | 516.1296 | 462.997 | Note 1 | 28.425 | 6.4516 | 497.8736 | 18.256 | -7.1879 | 25.4439 | 53.1326 | 72.22 | 6779 | 105.18 | 4615883.89 | 10.04 | 4776.62 | 54.0372 | -72166.61 | 121535.75 | VPC | 10.29% | 4.679% | -2.905 | 10.2831 | N/A | 25.4439 | 0.47086 | 40.951 | Water imported | Unbilled metered | Total annual cost of operating water system
Upson County Water Department | GA2930010 | Upson | 4878 | 151.687 | 3.649 | 0 | 155.336 | 115.227 | 0 | 0.3296 | 1.9417 | 117.4983 | 37.8377 | 4.2503 | 33.5874 | 40.109 | 71.6 | 1976 | 82.5 | 1244941.8 | 7.39 | 1774.48 | 20.5896 | 31409.89 | 59600.13 | VPC | 25.82% | 7.634% | 5.8931 | N/A | 1285.1985 | 33.5874 | 1.6313 | 58.0377 | Volume from own sources | Unbilled metered | Customer metering inaccuracies
USA - Fort Stewart | GA1790024 | Liberty | 27573 | 502.78 | 0 | 0 | 497.802 | 0.04 | 0.35 | 0.001 | 6.2225 | 6.6135 | 491.1885 | 1.2468 | 489.9417 | 497.412 | 161.7 | 2677 | 57 | 399909 | 2.93 | 0.06 | 26.5544 | 3653.02 | 29.4 | VPC | 99.92% | 0.9209% | 1.276 | N/A | 8301.2122 | 489.9417 | 18.4505 | 51.5017 | Volume from own sources | Billed metered | Customer metering inaccuracies
USA - Hunter Army Airfield - Main | GA0510107 | Chatham | 7500 | 128.68 | 1.02 | 0 | 128.4158 | 0.023 | 0.06 | Note 1 | 1.6052 | 1.6882 | 126.7276 | 0.32231 | 126.4053 | 128.3328 | 66.4 | 980 | 55 | 130664 | 1.2 | 0.21 | 10.1624 | 386.77 | 26.55 | VPC | 99.94% | 0.3166% | 0.90106 | N/A | 5215.6022 | 126.4053 | 12.4385 | 49.8445 | Volume from own sources | Billed metered | Customer metering inaccuracies
USA - Kings Bay Naval Base/UEM | GA0390013 | Camden | 9730 | 269.52 | 0 | 0 | 269.52 | 137.444 | 109.317 | 0 | 3.369 | 250.13 | 19.39 | 2.001 | 17.389 | 22.759 | 100 | 800 | 101 | 844476.63 | 12.95 | 327.66 | 24.9961 | 25912.95 | 5697.68 | VPC | 8.444% | 3.874% | 6.8527 | N/A | 476.411 | 17.389 | 0.69567 | 72.7941 | Billed metered | Billed unmetered | Customer metering inaccuracies
USAF - Mody Air Force Base | GA1850125 | Lowndes | 6500 | 101.511 | 0 | 0 | 101.511 | Note 1 & A | Note 1 | 25.579 | 1.2689 | 26.8479 | 74.6631 | 0.51215 | 74.151 | 101.511 | 50.8 | 493 | 65 | 250765 | 3.01 | 335.36 | Note 3 | 1541.58 | 24867.27 | VPC | 100% | 14.12% | 2.8462 | N/A | 3999.0811 | 74.151 | Note 3 | 61.5349 | Volume from own sources | Customer metering inaccuracies | Systematic data handling errors
USAF - Robins Air Force Base - Main | GA1530042 | Houston | 21462 | 555.3 | 0 | 0 | 533.9423 | 96.34 | 347.9 | 13.92 | 6.6743 | 464.8343 | 69.108 | 2.6894 | 66.4186 | 89.7023 | 92 | 1663 | 65 | 734538 | 1.52 | 1520 | 17.7266 | 4082.57 | 100823.41 | CRUC | 16.8% | 18.54% | 4.4308 | N/A | 1977.921 | 66.4186 | 3.7468 | 41.9737 | Volume from own sources | Billed unmetered | Billed metered
USMC Marine Corps Logistics Base Albany | GA0950035 | Dougherty | 3350 | 117.158 | 0 | 0 | 112.6519 | 32.12 | 17.41 | 0 | 1.4081 | 50.9381 | 61.7138 | 0.68637 | 61.0274 | 63.1219 | 39 | 320 | 66.2 | 173069 | 0.32 | 361.15 | Note 3 | 219.64 | 22040.05 | VPC | 56.03% | 13.16% | 5.8765 | N/A | 4287.1373 | 61.0274 | Note 3 | 31.5739 | Volume from own sources | Billed metered | Billed unmetered
Utilities, Inc. of Georgia (Big Canoe Subdivision) | GA2270004 | Pickens | 6396 | 282.87 | 20.35 | 1.221 | 301.999 | 87.977 | 0 | 2.6 | 3.775 | 94.352 | 207.647 | 10.483 | 197.164 | 214.022 | 96 | 1735 | 150 | 773758 | 3.8 | 1069.74 | 42.6836 | 39835.49 | 749223.16 | CRUC | 70.87% | 105.1% | 16.5537 | N/A | 5626.8262 | 197.164 | 4.6192 | 33.8095 | Volume from own sources | Billed metered | Unbilled metered
Valdosta | GA1850002 | Lowndes | 51691 | 3230.2 | 0 | 23.264 | 3206.936 | 2319.55 | Note 1 | 1 | 40.0867 | 2360.6367 | 846.2993 | 19.6321 | 826.6672 | 887.386 | 440 | 23197 | 63 | 3214545 | 1.9 | 262.67 | 134.7496 | 37266.96 | 217140.67 | VPC | 27.67% | 8.25% | 2.3187 | 97.6351 | N/A | 826.6672 | 6.1348 | 57.6971 | Volume from own sources | Billed metered | Unbilled metered
Vidalia | GA2790002 | Toombs | 13050 | 534.622 | 0 | 0 | 534.8894 | 425.589 | 0 | 13.467 | 6.6861 | 445.7421 | 89.1473 | 11.3615 | 77.7858 | 109.3004 | 141 | 7054 | 46 | 762761 | 2.74 | 240.58 | 30.5731 | 31130.57 | 18713.71 | VPC | 20.43% | 7.17% | 4.4127 | 30.2115 | N/A | 77.7858 | 2.5443 | 73.4244 | Customer metering inaccuracies | Variable production cost (applied to Real Losses) | Volume from own sources
Vienna | GA0930004 | Dooly | 3973 | 717.587 | 0 | 0 | 717.587 | 573.0432 | 2 | 15 | 8.9698 | 599.0131 | 118.5739 | 12.1815 | 106.3924 | 142.5438 | 76 | 1452 | 56 | 433566.29 | 2.17 | 172.36 | 12.8559 | 26433.96 | 18337.79 | VPC | 19.86% | 11.28% | 22.9849 | N/A | 3835.3415 | 106.3924 | 8.2757 | 54.4474 | Volume from own sources | Unbilled metered | Customer metering inaccuracies
Villa Rica | GA0450006 | Carroll | 15667 | 478.111 | 151.199 | 0 | 629.31 | 498.408 | 0 | 16.098 | 7.8664 | 522.3724 | 106.9376 | 10.6544 | 96.2832 | 130.902 | 80.7 | 6433 | 83 | 1050183.19 | 6.15 | 868.84 | 42.4596 | 65524.63 | 83654.71 | VPC | 20.8% | 16.19% | 4.5376 | 41.0057 | N/A | 96.2832 | 2.2676 | 72.4216 | Volume from own sources | Customer metering inaccuracies | Billed metered
Walker County Water & Sewerage Authority | GA2950003 | Walker | 36000 | 1236.267 | 0 | 292.751 | 953.0465 | 603.878 | 0 | 0.001 | 11.9131 | 615.7921 | 337.2544 | 16.2164 | 321.038 | 349.1685 | 429.4 | 11164 | 115 | 3198560.07 | 4.68 | 399.84 | 167.8015 | 75892.62 | 128363.84 | VPC | 36.64% | 6.535% | 3.9796 | N/A | 2048.3377 | 321.038 | 1.9132 | 62.0249 | Volume from own sources | Unbilled metered | Water exported
Walthourville | GA1790020 | Liberty | 3858 | 113.27 | 0 | 0 | 113.27 | 91.889 | 0 | 0 | 1.4159 | 93.3049 | 19.9651 | 0.97465 | 18.9905 | 21.381 | 37 | 2315 | 44 | 321522 | 4.29 | 348.48 | 8.7916 | 4181.25 | 6617.8 | VPC | 18.88% | 3.512% | 1.1535 | 22.4746 | N/A | 18.9905 | 2.1601 | 39.9667 | Volume from own sources | Variable production cost (applied to Real Losses) | Customer metering inaccuracies
Walton County Water Department | GA2970008 | Walton | 38023 | 0 | 1593 | 357 | 1234.587 | 890 | 0 | 0 | 15.4323 | 905.4323 | 329.1547 | 9.6041 | 319.5506 | 344.587 | 546 | 16370 | 90 | 11206571 | 10.32 | 1365.41 | 177.6975 | 99114.02 | 436317.57 | VPC | 27.91% | 4.966% | 1.6074 | N/A | 1603.4452 | 319.5506 | 1.7983 | 78.6582 | Billed metered | Unauthorized consumption | Systematic data handling errors
Warner Robins | GA1530007 | Houston | 69498 | 2601.45 | 707.681 | 0 | 3309.131 | 2316.354 | Note 1 | Note 1 | 41.3641 | 2357.7181 | 951.4129 | 85.7035 | 865.7093 | 992.777 | 463.89 | 27155 | 62 | 6851228.54 | 1.96 | 583.28 | 148.9709 | 167978.91 | 504950.94 | VPC | 30% | 10.17% | 8.6468 | 87.3433 | N/A | 865.7093 | 5.8113 | 61.0575 | Volume from own sources | Water imported | Billed metered
Washington | GA3170002 | Wilkes | 4134 | 323.7 | 0 | 0 | 323.5382 | 215.0519 | 0 | 11.3121 | 4.0442 | 230.4082 | 93.13 | 13.2604 | 79.8697 | 108.4863 | 51.6 | 3067 | 80.5 | 1318003.54 | 6.73 | 734.71 | 21.7197 | 89242.28 | 58681.03 | VPC | 33.53% | 12.08% | 11.8454 | 71.3469 | N/A | 79.8697 | 3.6773 | 62.9699 | Billed metered | Unbilled metered | Customer metering inaccuracies
Waycross | GA2990002 | Ware | 19900 | 859.0674 | 0 | 0 | 826.0263 | 629.2125 | 0 | 20.456 | 10.3253 | 659.9938 | 166.0325 | 10.2004 | 155.8321 | 196.8139 | 140 | 7593 | 48 | 1372108 | 1.43 | 161.05 | 33.2241 | 14590.48 | 25096.77 | VPC | 23.83% | 3.254% | 3.6805 | 56.2278 | N/A | 155.8321 | 4.6903 | 55.1354 | Volume from own sources | Customer metering inaccuracies | Billed metered
Waynesboro | GA0330004 | Burke | 5813 | 283.194 | 0 | 0 | 277.6412 | 246.413 | 0 | 18.45 | 3.4705 | 268.3335 | 9.3077 | 6.7155 | 2.5922 | 31.2282 | 82.6 | 2321 | 45 | 856500 | 4.31 | 1192.87 | 13.0581 | 28943.82 | 3092.11 | VPC | 11.25% | 6.793% | 7.927 | N/A | 85.9783 | 2.5922 | 0.19851 | 69.3529 | Volume from own sources | Variable production cost (applied to Real Losses) | Customer metering inaccuracies
West Point | GA2850002 | Troup | 3929 | 403.698 | 9.566 | 0 | 411.9165 | 387.043 | 0 | 0 | 5.149 | 392.192 | 19.7246 | 3.9423 | 15.7822 | 24.8735 | 73 | 2235 | 60 | 1732308 | 4.2 | 404.64 | 15.9909 | 16548.24 | 66247.05 | CRUC | 6.038% | 6.027% | 4.8326 | N/A | 592.3152 | 15.7822 | 0.98695 | 69.392 | Volume from own sources | Customer metering inaccuracies | Variable production cost (applied to Real Losses)
White County Water & Sewerage Authority | GA3110072 | White | 4420 | 273.897 | 0 | 80.556 | 206.9429 | 154.329 | 0 | 13.182 | 2.5868 | 170.0978 | 36.8451 | 11.5954 | 25.2498 | 52.6139 | 165.2 | 2215 | 100 | 1788908 | 5.26 | 1818.63 | 44.7483 | 60991.65 | 45920 | VPC | 25.42% | 7.579% | 14.3423 | N/A | 418.7498 | 25.2498 | 0.56426 | 63.9374 | Volume from own sources | Customer metering inaccuracies | Billed metered
Winder | GA0130002 | Barrow | 32971 | 1477.236 | 4.229 | 0 | 1481.465 | 1183.416 | 0 | 13.461 | 66.821 | 1263.698 | 217.767 | 31.0883 | 186.6787 | 298.049 | 406.7 | 16325 | 82 | 10165334.19 | 7.88 | 434.6 | 139.1445 | 244975.52 | 81130.58 | VPC | 20.12% | 3.551% | 5.2174 | 31.3292 | N/A | 186.6787 | 1.3416 | 69.0979 | Volume from own sources | Customer metering inaccuracies | Variable production cost (applied to Real Losses)
Woodstock | GA0570003 | Cherokee | 10070 | 131.919 | 619.715 | 13.772 | 737.862 | 528.804 | 1.498 | 23.566 | 9.2233 | 563.0913 | 174.7707 | 4.5511 | 170.2197 | 207.56 | 75.2 | 6895 | 139.63 | 2952233.03 | 7.4 | 2845.83 | 73.4447 | 33677.78 | 484416.26 | VPC | 28.13% | 20.71% | 1.8084 | 67.6367 | N/A | 170.2197 | 2.3177 | 78.8596 | Water imported | Customer metering inaccuracies | Unauthorized consumption
Wrightsville | GA1670002 | Johnson | 3757 | 190.497 | 0 | 0 | 211.6633 | 143.365 | 0 | 0 | 2.6458 | 146.0108 | 65.6525 | 13.3541 | 52.2984 | 68.2983 | 157 | 940 | 65 | 945025 | 1.75 | 0.79 | 23.4965 | 23369.66 | 41.55 | VPC | 32.27% | 2.478% | 38.9219 | N/A | 912.6333 | 52.2984 | 2.2258 | 66.8141 | Volume from own sources | Billed metered | Customer metering inaccuracies
Explanatory Footnote for Empty Fields
| Note 1 | “Note 1” represents N/A. The utility does not have uses that fit into this category.
| Note 2 | “Note 2” indicates the utility does not know what the value for this parameter is.
| Note 3 | “Note 3” indicates that the intended value cannot be calculated. The software does not display a value of UARL or ILI for very small water systems with low connection density or low pressure water distribution system. In summary, the UARL or ILI calculation has not yet been proven as fully valid for very small or low pressure water distribution systems.
| Note 4 | “Note 4” indicates that the intended value cannot be calculated. The software does not display a value for “Annual Cost of Real Losses” because the utility does not know what the value for the “variable production cost” is.
| Note A | Moody Air force Base only consumes its water and does no billing. They also randomly meter certain buildings. Most of the older buildings have no meter in place
| Note B | The variable production cost is not applicable to this utility. Water supply is entirely purchased as bulk water imported at a defined rate. No restriction applies for volume and there are no provisions on any rate adjustment for variable production cost. The City of Griffin does the entire meter reading for Spalding County. This cost is built in through a complex rate structure based on the contract between the County and City. In summary, Spalding County does not know the value for this field.
Yellow represent negative values (anomalies). Both the utilities and EPD are aware of these negative values (i.e. negative real losses and negative ILI values). These negative values are not creditable. They are mostly due to extreme meter inaccuracies. For example, (a) over-estimation of authorized consumption, and/or (b) under-estimation of water supply, and/or (c) over-estimation of apparent losses. To resolve this issue, the utilities with negative values must (a) replace their old meters with new ones, and/or (b) perform high frequency (short intervals) recalibration and accuracy testing on a regular basis.