## Final
Name of City / Utility: 2022 Validated Water Audit | WSID Number | Service County | Water System Service Population | Volume From Own Sources | Water Imported | Water Exported | Water Supplied | Billed Metered | Billed Unmetered | Unbilled Metered | Unbilled Unmetered | Authorized Consumption | Water Losses | Annual Volume of Apparent Losses | Annual Volume of Real Losses | Non Revenue Water | Length of Mains | Number of Active and Inactive Service Connections | Average Operating Pressure | Total Annual Cost of Operating Water System | Customer Retail Unit Cost | Variable Production Cost | Unavoidable Annual Real Losses (UARL) vol/Yr | Annual Volume of NRW | Annual Cost of Apparent Losses | Annual Cost of Real Losses | Annual Cost of NRW | Value Applied to Real Losses (VPC / CRUC) | Unit Apparent Losses Vol/conn/day | Unit Real Losses Vol/conn/day | Unit Real Losses per length of main per day | Total Loss Cost Rate $/conn/yr | Apparent Loss Cost Rate $/conn/yr | Real Loss Cost Rate $/conn/yr | Infrastructure Leakage Index (ILI) | Water Audit Data Validity Score
Adairsville | GA0150000 | Bartow | 9700 | 620.98 | 4.7474 | 200.5803 | 434.4242 | 297.1253 | 0.036 | 6.9981 | 0.7429 | 304.9023 | 129.5219 | 10.8917 | 118.6302 | 137.2629 | 89.3 | 3593 | 70 | Note 5 | 9.51 | 785.4975 | 26.1137 | 137.2629 | 101691.63 | 93183.75 | 200955.92 | VPC | 8.3051 | 90.4577 | 3639.5785 | 54.2375 | 28.3027 | 25.9348 | 4.5428 | 78
Adel | GA0750000 | Cook | 5600 | 373.765 | Note 1 | Note 1 | 373.765 | 294.165 | Note 1 | 0.758 | 4.6721 | 299.5951 | 74.1699 | 4.6488 | 69.5211 | 79.6 | 74.5 | 3058 | 54 | 875605 | 2.34 | 3.25 | 16.985 | Note 6 | 10878.3 | 162679.36 | 173575.31 | CRUC | 4.165 | 62.2854 | 2556.6275 | 56.7553 | 3.5573 | 53.198 | 4.0931 | 60
Alamo | GA3090000 | Wheeler | 3260 | 146.767 | Note 1 | Note 1 | 145.3139 | 129.502 | Note 1 | 1.61 | 0.32376 | 131.4358 | 13.8781 | 3.3233 | 10.5548 | 15.8119 | 25 | 358 | 45 | 227830.67 | 3.94 | 264.38 | 3.1035 | 15.8119 | 12972.89 | 2790.49 | 16274.63 | VPC | 25.4325 | 80.7748 | 1156.6949 | 44.0318 | 36.2371 | 7.7947 | 3.4009 | 67
Albany | GA0950000 | Dougherty | 92208 | 4671.79 | Note 1 | Note 1 | 4869.4913 | 3567.83 | Note 1 | 50.58 | 34.75 | 3653.16 | 1216.3313 | 91.6843 | 1124.6471 | 1301.6613 | 678 | 38451 | 55 | 10394784 | 5.7 | 269.08 | 189.4203 | 1301.6613 | 516994.2 | 6410488.45 | 7413863.65 | CRUC | 6.5327 | 80.1338 | 4544.5795 | 180.1639 | 13.4455 | 166.7184 | 5.9373 | 61
Alma | GA0050000 | Bacon | 5419 | 201.701 | Note 1 | Note 1 | 205.6075 | 153.54 | Note 1 | 19.25 | 21.054 | 193.844 | 11.7635 | 3.5292 | 8.2344 | 52.0675 | 48 | 2007 | 60 | 412076 | 5.78 | 196.15 | 12.28 | Note 6 | 20398.71 | 1615.17 | 29919.51 | VPC | 4.8176 | 11.2406 | 469.9974 | 10.9686 | 10.1638 | 0.80477 | 0.67055 | 64.9451
Americus | GA2610000 | Sumter | 14612 | 940.845 | Note 1 | Note 1 | 940.2076 | 642.7275 | Note 1 | 0.18732 | 1.6068 | 644.5217 | 295.6859 | 30.0018 | 265.6841 | 297.48 | 148 | 7993 | 62 | 2048766 | 4.0326 | 303.6327 | 45.2516 | 297.48 | 120955.88 | 80670.38 | 202171.02 | VPC | 10.2836 | 91.0674 | 4918.2552 | 25.2254 | 15.1327 | 10.0926 | 5.8713 | 58
Ashburn | GA2870000 | Turner | 7052 | 249.178 | Note 1 | Note 1 | 311.4725 | 200.975 | Note 1 | 8.066 | 11.42 | 220.461 | 91.0115 | 19.1824 | 71.8291 | 110.4975 | 57.7 | 2612 | 47.5 | 570417 | 2.66 | 260.14 | 12.2049 | 110.4975 | 49341.82 | 18685.63 | 73096.54 | VPC | 20.1204 | 75.3416 | 3410.6098 | 26.0442 | 18.8904 | 7.1538 | 5.8853 | 75
Athens-Clarke County Public Utilities Dept | GA0590000 | Clarke | 127000 | 4879.73 | Note 1 | Note 1 | 4831.4158 | 4442.892 | Note 1 | 112.174 | 11.1072 | 4566.1732 | 265.2426 | 68.2252 | 197.0174 | 388.5238 | 820.91 | 43263 | 94.96 | 8586546.22 | 6.41 | 411.53 | 378.858 | 388.5238 | 430527.02 | 81078.56 | 562339.51 | VPC | 4.3205 | 12.4766 | 657.5309 | 11.8255 | 9.9514 | 1.8741 | 0.52003 | 80
Atlanta | GA1210001 | Fulton | 1200000 | 34556.16 | 5653.435 | 1694.2624 | 38681.5554 | 25401.2243 | 0.016 | Note 1 | 111.8748 | 25513.115 | 13168.4404 | 1211.0607 | 11957.3796 | 13280.3151 | 2809.17 | 219288 | 103.57 | 143966056.63 | 7.5936 | 354.81 | 1817.9793 | 13280.3151 | 9196342.67 | 4242597.87 | 13478634.82 | VPC | 15.1307 | 149.3923 | 11661.7877 | 61.2844 | 41.9373 | 19.3472 | 6.5773 | 79
Auburn | GA0130000 | Barrow | 9134 | Note 1 | 228.389 | Note 1 | 226.539 | 171.823 | 6.123 | Note 1 | 2.8317 | 180.7777 | 45.7613 | 0.99591 | 44.7654 | 48.593 | 80.7 | 3383 | 50.3 | 2486241 | 15 | 550 | 17.332 | Note 6 | 14938.58 | 24620.95 | 41116.99 | VPC | 0.80653 | 36.2533 | 1519.7623 | 11.6936 | 4.4158 | 7.2778 | 2.5828 | 81.4608
Augusta Utilities | GA2450000 | Richmond | 200000 | 12804.896 | Note 1 | Note 1 | 12804.896 | 9402.549 | Note 1 | 625.774 | 70 | 10098.323 | 2706.573 | 251.6724 | 2454.9006 | 3402.347 | 1319.43 | 67873 | 87 | 53631410 | 6.57 | 301.29 | 549.967 | 3402.347 | 1573430.6 | 739636.99 | 2522697.35 | VPC | 10.1589 | 99.0932 | 5097.4701 | 34.0793 | 23.182 | 10.8974 | 4.4637 | 70
Austell | GA0670001 | Cobb | 7800 | Note 1 | 345.26 | Note 1 | 348.3253 | 304.07 | Note 1 | 3.8472 | 0.035 | 307.9522 | 40.3731 | 4.6306 | 35.7424 | 44.2553 | 62.88 | 3693 | 128 | 2197163 | 8.09 | 6363.79 | 41.7738 | 44.2553 | 37394.67 | 227457.37 | 289557.54 | VPC | 3.4353 | 26.5162 | 1557.3233 | 71.7173 | 10.1258 | 61.5915 | 0.85562 | 79
Bainbridge | GA0870001 | Decatur | 15444 | 858.818 | Note 1 | Note 1 | 858.818 | 551.427 | Note 1 | Note 1 | 10.7352 | 562.1622 | 296.6558 | 9.0956 | 287.5602 | 307.391 | 175 | 5720 | 58 | 310000 | 3.36 | 285 | 38.2066 | Note 6 | 30561.16 | 81954.65 | 115575.35 | VPC | 4.3565 | 137.7336 | 4501.9208 | 19.6706 | 5.3429 | 14.3277 | 7.5265 | 51.2333
Baldwin | GA1370001 | Habersham | 4848 | 791.21 | Note 1 | 566.946 | 223.7987 | 112.94 | Note 1 | 1.706 | 0.725 | 115.371 | 108.4277 | 0.40442 | 108.0233 | 110.8587 | 81.4 | 1846 | 103 | Note 5 | 0.86 | 1932.57 | 26.9659 | 110.8587 | 4413.29 | 208762.54 | 217873.91 | VPC | 0.60022 | 160.3219 | 3635.8007 | 115.4799 | 2.3907 | 113.0891 | 4.0059 | 81
Baldwin County Water & Sewer | GA0090000 | Baldwin | 4984 | Note 1 | 720.515 | 5.307 | 715.1544 | 538.937 | Note 1 | 21.802 | 8.9394 | 569.6784 | 145.476 | 20.4777 | 124.9983 | 176.2174 | 423 | 9752 | 60 | 3852200 | 8.14 | 2208.64 | 82.1519 | Note 6 | 166688.25 | 276076.23 | 510661.23 | VPC | 5.753 | 35.117 | 809.6006 | 45.4024 | 17.0927 | 28.3097 | 1.5216 | 69.5045
Banks County | GA0110026 | Banks | 8696 | 250.49 | 33.98 | 31.6 | 258.3563 | 225.036 | Note 1 | 23.248 | 3.2295 | 251.5135 | 6.8429 | 2.4561 | 4.3867 | 33.3203 | 336 | 3221 | 99 | 1479126.09 | 6.67 | 892.74 | 83.1434 | Note 6 | 16382.45 | 3916.21 | 43936.14 | VPC | 2.0891 | 3.7313 | 35.7691 | 6.302 | 5.0861 | 1.2158 | 0.052761 | 63.9906
Barnesville | GA1710000 | Lamar | 12533 | 694.36 | Note 1 | 35.08 | 636.25 | 336.271 | Note 1 | 59.175 | 0.84068 | 396.2867 | 239.9633 | 13.9116 | 226.0517 | 299.979 | 82 | 4642 | 85 | Note 5 | 6.38 | 372.96 | 35.366 | 299.979 | 77762.47 | 84308.23 | 184454.16 | VPC | 8.2107 | 133.4166 | 7552.6789 | 34.914 | 16.7519 | 18.162 | 6.3918 | 60
Barrow County Water System / Barrow Co. BOC Transmission Mains | GA0130031 / GA0130034 | Barrow | 17133 | Note 1 | 794.831 | 343.973 | 447.7981 | 384.106 | Note 1 | 0.082 | 2.373 | 386.561 | 61.2371 | 1.2302 | 60.0069 | 63.6921 | 163.13 | 6724 | 114.8 | 3607035 | 0.05 | 748.23 | 79.2423 | 63.6921 | 12365.22 | 44898.94 | 59101.07 | VPC | 0.50126 | 24.4501 | 1007.7999 | 8.5164 | 1.839 | 6.6774 | 0.75726 | 56
Bartow County Water Department | GA0015001 | Bartow | 62875 | 69.517 | 2745.619 | 21.496 | 2837.2741 | 1858.388 | Note 1 | Note 1 | 5.6516 | 1864.0396 | 973.2345 | 37.5923 | 935.6422 | 978.8861 | 970.6 | 24183 | 122 | 18296403.57 | 8.6229 | 3101.6065 | 395.355 | 978.8861 | 324154.48 | 2901994.09 | 3243677.64 | VPC | 4.2589 | 106.0002 | 2641.0503 | 133.4056 | 13.4042 | 120.0014 | 2.3666 | 57
Baxley | GA0010000 | Appling | 9018 | 258.005 | Note 1 | Note 1 | 261.0462 | 208.064 | Note 1 | 17.201 | 3.2631 | 228.5281 | 32.5181 | 8.1397 | 24.3784 | 52.9822 | 108.4 | 3340 | 59 | 626592 | 3.83 | 417.3 | 23.4181 | Note 6 | 31175.18 | 10173.1 | 49887.94 | VPC | 6.6768 | 19.997 | 616.1446 | 12.3797 | 9.3339 | 3.0458 | 1.041 | 74.3889
Blackshear | GA2290000 | Pierce | 3489 | 185.558 | Note 1 | Note 1 | 189.3449 | 157.32 | Note 1 | 0.21 | 2.3668 | 159.8968 | 29.4481 | 3.2153 | 26.2328 | 32.0249 | 36 | 2245 | 50 | 1099552.8 | 4.91 | 292.11 | 9.7001 | Note 6 | 15787.1 | 7662.86 | 24202.67 | VPC | 3.9238 | 32.0137 | 1996.4072 | 10.4454 | 7.0321 | 3.4133 | 2.7044 | 78.1765
Blairsville | GA2910000 | Union | 5078 | 224.134 | Note 1 | Note 1 | 228.8506 | 143.166 | Note 1 | 4.088 | 1.024 | 148.278 | 80.5726 | 1.0849 | 79.4877 | 85.6846 | 74.6 | 1924 | 98 | Note 5 | 8.66 | 700.43 | 24.7595 | 85.6846 | 9313.58 | 55675.59 | 68569.76 | VPC | 1.5449 | 113.1885 | 2919.2304 | 33.7782 | 4.8407 | 28.9374 | 3.2104 | 74
Blakely | GA0990000 | Early | 7036 | 325.723 | Note 1 | Note 1 | 360.0741 | 172.068 | Note 1 | 3.145 | 0.43017 | 175.6432 | 184.4309 | 16.0963 | 168.3346 | 188.0061 | 56 | 2706 | 53 | 223000 | 5.41 | 271.82 | 13.7129 | 188.0061 | 85675.55 | 45756.72 | 132404.07 | VPC | 16.2969 | 170.4327 | 8235.55 | 48.5707 | 31.6613 | 16.9094 | 12.2756 | 80
Blue Ridge Water & Sewer | GA1110000 | Fannin | 7500 | 316.96 | Note 1 | 14.07 | 308.8088 | 186.49 | Note 1 | 0.648 | 0.18 | 187.318 | 121.4908 | 1.9474 | 119.5434 | 122.3188 | 136 | 3654 | 100 | 2808136.02 | 9.03 | 787.9 | 46.8609 | 122.3188 | 17546.2 | 94188.22 | 112386.8 | VPC | 1.4601 | 89.6322 | 2408.2064 | 30.5787 | 4.8019 | 25.7767 | 2.551 | 83
Bowdon | GA0450000 | Carroll | 6529 | 188.886 | 3.194 | Note 1 | 196.9232 | 127.515 | Note 1 | 1.428 | 2.001 | 130.944 | 65.9792 | 1.94 | 64.0392 | 69.4082 | 141 | 2418 | 77 | 1053065 | 6.05 | 585.06 | 31.6325 | 69.4082 | 11658.35 | 37466.78 | 51131.3 | VPC | 2.1982 | 72.5599 | 1244.3253 | 20.3164 | 4.8215 | 15.4949 | 2.0245 | 81
Braselton Water System | GA1570000 | Jackson | 17369 | 214.032 | 416.914 | 23.598 | 596.7829 | 535.692 | Note 1 | 2.066 | 1.3392 | 539.0972 | 57.6857 | 2.6785 | 55.0072 | 61.0909 | 138 | 6433 | 98 | Note 5 | 9.95 | 2208.19 | 61.2214 | 61.0909 | 26650.68 | 121466.43 | 155636.5 | VPC | 1.1407 | 23.4268 | 1092.0635 | 23.0246 | 4.1428 | 18.8818 | 0.8985 | 44
Bremen | GA1430000 | Haralson | 6700 | 100.63 | 335.902 | 92.951 | 347.7661 | 238.066 | Note 1 | 0.02 | 0.59517 | 238.6812 | 109.0849 | 1.1903 | 107.8946 | 109.7001 | 76 | 3321 | 90 | Note 5 | 5.97 | 3665.39 | 29.8708 | 109.7001 | 7106.27 | 395475.81 | 404836.9 | VPC | 0.98199 | 89.0098 | 3889.4956 | 121.2232 | 2.1398 | 119.0834 | 3.612 | 75
Brunswick-Glynn Joint Water Sewer Commission | GA1270000 | Glynn | 49936 | 1841.014 | Note 1 | Note 1 | 1836.4229 | 1366.105 | Note 1 | 103.516 | 3.4153 | 1473.0363 | 363.3867 | 100.6361 | 262.7506 | 470.3179 | 344 | 19816 | 54 | 2979629 | 2.89 | 220.58 | 95.2671 | 470.3179 | 273200.45 | 57957.52 | 354744.87 | VPC | 13.9138 | 36.3274 | 2092.6295 | 16.7116 | 13.7869 | 2.9248 | 2.758 | 60
Brunswick-Glynn Joint Water Sewer Commission-St. Simons Island | GA1270001 | Glynn | 28728 | 1048.523 | Note 1 | Note 1 | 1045.9082 | 780.331 | Note 1 | 29.347 | 1.9508 | 811.6288 | 234.2794 | 55.5832 | 178.6962 | 265.5772 | 158 | 11400 | 56 | 1697005 | 2.89 | 220.58 | 52.4241 | 265.5772 | 155635.14 | 39416.8 | 201955.62 | VPC | 13.3581 | 42.9455 | 3098.5984 | 17.1098 | 13.6522 | 3.4576 | 3.4087 | 60
Buford | GA1350000 | Gwinnett | 10519 | 434.654 | 6.274 | Note 1 | 440.928 | 378.148 | 2.028 | 5.519 | 0.95044 | 386.6454 | 54.2826 | 19.6852 | 34.5974 | 60.752 | 81 | 3896 | 61 | 14953061.83 | 2.53 | 430.99 | 22.7684 | 60.752 | 49266.51 | 14911.13 | 66965.9 | VPC | 13.8429 | 24.3294 | 1170.2144 | 16.4727 | 12.6454 | 3.8273 | 1.5195 | 63
Butts County, et al. Water & Sewer Authority/Jackson/Jenkinsburg | GA0350051 | Butts | 25781 | 913.682 | 0.912 | 80.314 | 834.28 | 605.97 | Note 1 | 0.18 | 1.5149 | 607.6649 | 226.6151 | 9.1526 | 217.4625 | 228.31 | 290 | 6892 | 75 | Note 5 | 6.5 | 624.92 | 71.2489 | 228.31 | 59481.07 | 135896.66 | 196436.93 | VPC | 3.6384 | 86.4463 | 2054.4402 | 28.3485 | 8.6305 | 19.718 | 3.0522 | 64
Byron | GA2250000 | Peach | 9552 | 297.568 | Note 1 | Note 1 | 294.6218 | 236.195 | Note 1 | Note 1 | 3.6828 | 239.8778 | 54.744 | 1.327 | 53.417 | 58.4268 | 75.6 | 3538 | 60 | 776980 | 5 | 396.74 | 20.5793 | Note 6 | 6635.21 | 21192.65 | 29288.96 | VPC | 1.0276 | 41.3646 | 1935.8182 | 7.8654 | 1.8754 | 5.99 | 2.5957 | 57.1529
Cairo | GA1310000 | Grady | 10000 | 559.01 | Note 1 | Note 1 | 540.1063 | 399.81 | Note 1 | Note 1 | 0.99952 | 400.8095 | 139.2968 | 6.0375 | 133.2592 | 140.2963 | 125 | 4535 | 70 | 420183 | 1.85 | 751.53 | 34.6586 | 140.2963 | 11169.44 | 100148.3 | 112068.91 | VPC | 3.6475 | 80.5058 | 2920.75 | 24.5464 | 2.4629 | 22.0834 | 3.8449 | 54
Calhoun | GA1290000 | Gordon | 59600 | 3995.782 | Note 1 | 1028.784 | 2956.6737 | 2108.836 | Note 1 | Note 1 | 5.2721 | 2114.1081 | 842.5656 | 74.1981 | 768.3675 | 847.8377 | 864.93 | 22932 | 109.1 | 12907022.94 | 4.89 | 361.41 | 323.3136 | 847.8377 | 362828.88 | 277695.68 | 642429.95 | VPC | 8.8646 | 91.7982 | 2433.8575 | 27.9315 | 15.8219 | 12.1095 | 2.3765 | 71
Camilla Water Department | GA2050001 | Mitchell | 5500 | 991.047 | Note 1 | Note 1 | 991.047 | 775.778 | Note 1 | Note 1 | 1.9394 | 777.7174 | 213.3296 | 44.7093 | 168.6202 | 215.269 | 72 | 2879 | 57 | 1258919 | 3.62 | 94.842 | 17.0886 | 215.269 | 161847.71 | 15992.28 | 178023.93 | VPC | 42.5465 | 160.4631 | 6416.2954 | 61.7714 | 56.2166 | 5.5548 | 9.8674 | 61
Canton | GA0570001 | Cherokee | 27048 | 1319.84 | 67.51 | 127.954 | 1303.0271 | 923.727 | Note 1 | 16.889 | 2.3093 | 942.9253 | 360.1018 | 23.8149 | 336.2869 | 379.3001 | 150 | 10300 | 80 | Note 5 | 7.44 | 608.1 | 68.8098 | 379.3001 | 174827.93 | 204496.05 | 390998.48 | VPC | 6.3346 | 89.4499 | 6142.2261 | 36.8276 | 16.9736 | 19.854 | 4.8872 | 56
Carroll County Water Authority | GA0450001 | Carroll | 48941 | 1907.243 | 10.472 | 470.329 | 1447.9272 | 1105.534 | Note 1 | 8.826 | 43.142 | 1157.502 | 290.4252 | 17.6398 | 272.7854 | 342.3932 | 803.1 | 20907 | 97 | 9057161 | 8.53 | 433.5 | 264.8585 | Note 6 | 150467.62 | 118252.46 | 291248.21 | VPC | 2.3116 | 35.7467 | 930.5905 | 12.8531 | 7.197 | 5.6561 | 1.0299 | 62.465
Carrollton | GA0450002 | Carroll | 26853 | 1790.99 | Note 1 | 2.5387 | 1784.8714 | 1431.7745 | Note 1 | 46.972 | 21.18 | 1499.9265 | 284.9449 | 7.1589 | 277.786 | 353.0969 | 246.3 | 11136 | 80 | 4524335.2 | 6.79 | 483.33 | 87.6842 | 353.0969 | 48608.74 | 134262.32 | 215810.97 | VPC | 1.7613 | 68.3421 | 3089.9618 | 16.4216 | 4.365 | 12.0566 | 3.168 | 69
Cartersville Water Department | GA0150002 | Bartow | 31572 | 4737.14 | Note 1 | 2387.333 | 2379.8402 | 1728.152 | Note 1 | Note 1 | 4.3204 | 1732.4724 | 647.3678 | 62.0888 | 585.2791 | 651.6882 | 237 | 12143 | 113 | 6514720.77 | 3.74 | 160.63 | 128.0088 | 651.6882 | 310422.24 | 94013.37 | 405129.6 | VPC | 14.0086 | 132.0517 | 6765.8407 | 33.3061 | 25.5639 | 7.7422 | 4.5722 | 56
Catoosa Utility District Authority | GA0470000 | Catoosa | 52650 | 1361.484 | 541.207 | 64.754 | 1855.1534 | 1474.218 | Note 1 | Note 1 | 23.1894 | 1497.4074 | 357.746 | 23.2145 | 334.5315 | 380.9354 | 563 | 21462 | 113 | 6924933 | 4.12 | 189.6 | 258.4053 | Note 6 | 95643.82 | 63427.17 | 163467.7 | VPC | 2.9634 | 42.7045 | 1627.9299 | 7.4118 | 4.4564 | 2.9553 | 1.2946 | 70.9915
Cave Spring | GA1150000 | Floyd | 3500 | 285.988 | 0.099 | 92.992 | 193.5789 | 86.219 | 27.359 | 8.074 | 0.28395 | 121.9359 | 71.643 | 2.7383 | 68.9047 | 80.0009 | 87 | 2080 | 114.9 | 1151393.09 | 4.65 | 218.38 | 32.824 | 80.0009 | 11909.57 | 15047.41 | 28782.19 | VPC | 3.6068 | 90.7596 | 2169.8846 | 12.9601 | 5.7258 | 7.2343 | 2.0992 | 77
Cedartown | GA2330000 | Polk | 9750 | 440.25 | Note 1 | Note 1 | 435.8911 | 318.0553 | Note 1 | 48.9344 | 0.79514 | 367.7848 | 68.1063 | 9.0799 | 59.0264 | 117.8358 | 85.9 | 4014 | 85 | Note 5 | 8.29 | 203.97 | 33.0981 | 117.8358 | 67196.84 | 12039.62 | 89379.8 | VPC | 6.1974 | 40.2881 | 1882.6107 | 19.74 | 16.7406 | 2.9994 | 1.7834 | 62
Centerville | GA1530000 | Houston | 11094 | 491.005 | 29.653 | Note 1 | 520.5598 | 310.248 | Note 1 | 13.896 | 6.507 | 330.651 | 189.9088 | 12.1021 | 177.8067 | 210.3118 | 53 | 4507 | 65 | 1998601.17 | 4 | 368.72 | 22.842 | Note 6 | 48408.37 | 65560.9 | 121492.26 | VPC | 7.3566 | 108.0856 | 9191.3533 | 25.2872 | 10.7407 | 14.5465 | 7.7842 | 50.2367
Chatsworth Water Works Commission | GA2130000 | Murray | 30500 | 595.83 | 582.925 | 0.992 | 1177.8848 | 837.376 | Note 1 | 16.841 | 2.0934 | 856.3104 | 321.5744 | 12.8153 | 308.7591 | 340.5088 | 430 | 12092 | 90 | 5300407 | 7.1 | 830.64 | 136.0023 | 340.5088 | 89922.39 | 256467.63 | 362117.72 | VPC | 2.9036 | 69.9566 | 1967.2448 | 28.6462 | 7.4365 | 21.2097 | 2.2702 | 70
Chattooga CountY Water District 1 | GA0550000 | Chattoga | 7800 | 344.8538 | 10.1952 | 8.6688 | 346.5145 | 203.8865 | Note 1 | Note 1 | 0.50972 | 204.3962 | 142.1183 | 11.7503 | 130.368 | 142.628 | 300 | 3460 | 90 | Note 5 | 16.124 | 508.775 | 70.3647 | 142.628 | 189462.29 | 66327.98 | 256049.6 | VPC | 9.3042 | 103.2291 | 1190.5753 | 73.9278 | 54.7579 | 19.1699 | 1.8527 | 51
Cherokee County Water & Sewerage Authority | GA0570002 | Cherokee | 228903 | 7014.6229 | 0.792 | 601.85 | 6413.8535 | 5470.846 | Note 1 | 188.5056 | 13.6771 | 5673.0288 | 740.8247 | 102.4159 | 638.4087 | 943.0075 | 1349.8 | 77011 | 107.3 | 38657449 | 6.01 | 277.75 | 738.4101 | 943.0075 | 599621.16 | 177318.03 | 833095.45 | VPC | 3.6435 | 22.7119 | 1295.7957 | 10.0887 | 7.7862 | 2.3025 | 0.86457 | 85
Chickamauga | GA2950000 | Walker | 6102 | 294.34 | 6.999 | Note 1 | 316.9516 | 155.819 | Note 1 | 11.778 | 3.9619 | 171.5589 | 145.3927 | 4.6023 | 140.7905 | 161.1326 | 41.9 | 2347 | 145 | 593289 | 3.54 | 327.49 | 30.6292 | Note 6 | 16292.05 | 46107.46 | 67554.17 | VPC | 5.3724 | 164.3491 | 9205.9013 | 26.5869 | 6.9416 | 19.6453 | 4.5966 | 46.314
Clarkesville | GA1370002 | Habersham | 5875 | 221.41 | 2 | Note 1 | 225.6465 | 147.428 | 12.092 | 11.5037 | 0.3988 | 171.4225 | 54.2239 | 40.5305 | 13.6934 | 66.1265 | 61.5 | 2225 | 76.1 | 993343 | 6.33 | 381.02 | 18.5121 | 66.1265 | 239449.41 | 5217.46 | 249201.97 | VPC | 49.9068 | 16.8612 | 610.0189 | 109.9626 | 107.6177 | 2.3449 | 0.7397 | 62
Claxton | GA1090001 | Evans | 3840 | 171.815 | Note 1 | Note 1 | 173.8139 | 109.661 | Note 1 | 16.141 | 0.27415 | 126.0762 | 47.7377 | 1.819 | 45.9187 | 64.1529 | 43 | 1797 | 60 | 1219900 | 4.74 | 451.47 | 10.9977 | 64.1529 | 7923.01 | 20730.9 | 36064.86 | VPC | 2.7733 | 70.0081 | 2925.6881 | 15.9454 | 4.409 | 11.5364 | 4.1753 | 69
Clayton | GA2410000 | Rabun | 7225 | Note 1 | 432.3943 | 14.0063 | 401.1398 | 166.8355 | Note 1 | 8.3055 | 0.41709 | 175.5581 | 225.5817 | 7.1864 | 218.3952 | 234.3043 | 130 | 3647 | 160 | Note 5 | 21.31 | 3718.8001 | 73.0204 | 234.3043 | 147843.96 | 812168.27 | 992449.94 | VPC | 5.3987 | 164.0645 | 4602.6396 | 263.2334 | 40.5385 | 222.6949 | 2.9909 | 59
Clayton County Water Authority | GA0630000 | Clayton | 303287 | 10248.98 | 30.992 | 203.66 | 10073.2382 | 7825.449 | 0.746 | 16.526 | 14.093 | 7856.814 | 2216.4242 | 19.7235 | 2196.7007 | 2247.0432 | 1379.17 | 89793 | 98.7 | 35224128 | 4.66 | 402.16 | 754.0231 | 2247.0432 | 91910.78 | 883425.17 | 987649.69 | VPC | 0.60179 | 67.0248 | 4363.7537 | 10.862 | 1.0236 | 9.8385 | 2.9133 | 72
Cleveland | GA3110000 | White | 4906 | 177.598 | 119.619 | 16.048 | 278.9036 | 189.7483 | Note 1 | 0.21623 | 0.47437 | 190.4389 | 88.4647 | 5.8196 | 82.645 | 89.1553 | 50 | 2378 | 90.7 | 2000205 | 7.25 | 1590.321 | 20.7638 | 89.1553 | 42160.92 | 131432.15 | 174691.34 | VPC | 6.7049 | 95.2165 | 4528.4956 | 72.9996 | 17.7296 | 55.27 | 3.9803 | 67
Cobb County Water System / Cobb County-Marietta Water Authority | GA0670003 / GA0670002 | Cobb | 695000 | 28576.482 | Note 1 | 6668.44 | 22028.2209 | 20066 | Note 1 | Note 1 | 26.338 | 20092.338 | 1935.8829 | 221.4527 | 1714.4302 | 1962.2209 | 3260 | 197313 | 118 | 166281214 | 5.45 | 2255.3 | 2034.349 | 1962.2209 | 1206917.41 | 3866554.34 | 5132871.85 | VPC | 3.0749 | 23.8052 | 1440.8187 | 25.7128 | 6.1168 | 19.596 | 0.84274 | 75
Cochran | GA0230000 | Bleckley | 6297 | 265.38 | Note 1 | Note 1 | 272.1846 | 124.394 | 0.261 | 1.275 | 0.31164 | 126.2416 | 145.943 | 3.1879 | 142.755 | 147.5296 | 64 | 2761 | 53 | Note 5 | 7.18 | 311.95 | 14.7097 | 147.5296 | 22710.76 | 44532.43 | 67738.14 | VPC | 3.1634 | 141.6551 | 6111.0886 | 24.3547 | 8.2256 | 16.1291 | 9.7048 | 60
College Park | GA1210002 | Fulton | 14000 | 298 | 1131 | Note 1 | 1413.398 | 859 | 54 | 11 | 2.2825 | 926.2825 | 487.1155 | 6.7455 | 480.3701 | 500.398 | 99 | 3102 | 69 | 5638669 | 4.69 | 3893 | 25.2074 | 500.398 | 31614.19 | 1870080.75 | 1953403.72 | VPC | 5.9577 | 424.269 | 13293.762 | 613.0545 | 10.1916 | 602.8629 | 19.0567 | 54
Columbia County Water Utility | GA0730000 | Columbia | 135000 | 6625.56 | Note 1 | 453.971 | 6166.2474 | 5469.961 | Note 1 | 70.62 | 19.674 | 5560.255 | 605.9924 | 51.8361 | 554.1563 | 696.2864 | 887.18 | 52704 | 52.03 | Note 5 | 3.77 | 577.2 | 241.2846 | 696.2864 | 194425.62 | 319859.01 | 566402.33 | VPC | 2.6946 | 28.8069 | 1711.3059 | 9.758 | 3.689 | 6.069 | 2.2967 | 75
Columbus Water Works | GA2150000 | Muscogee | 206922 | 11268.078 | 5.684 | 1230.374 | 9974.1881 | 7589.375 | Note 1 | 559.2171 | 18.9734 | 8167.5655 | 1806.6226 | 256.3248 | 1550.2978 | 2384.8131 | 1151 | 72645 | 87 | 19928063.34 | 2.06 | 270.35 | 543.7618 | 2384.8131 | 668653.14 | 419123.02 | 1244089.97 | VPC | 9.667 | 58.4678 | 3690.1749 | 14.9739 | 9.2044 | 5.7695 | 2.8511 | 74
Commerce | GA1570001 | Jackson | 11000 | 830.115 | 20.428 | 123.8448 | 726.6982 | 387.5741 | Note 1 | Note 1 | 0.96894 | 388.543 | 338.1552 | 1.9379 | 336.2173 | 339.1241 | 130.06 | 4115 | 66 | Note 5 | 5.01 | 667.33 | 31.8199 | 339.1241 | 9708.73 | 224367.89 | 234723.22 | VPC | 1.2902 | 223.8501 | 7082.4487 | 56.8837 | 2.3594 | 54.5244 | 10.5663 | 67
Coosa Water Authority | GA2910006 | Union | 5730 | 125.797 | Note 1 | Note 1 | 125.1711 | 89.541 | Note 1 | 0.53 | 0.22385 | 90.2949 | 34.8763 | 0.71873 | 34.1576 | 35.6301 | 180 | 3500 | 152 | 92691.13 | 4.39 | 740.51 | 83.1534 | 35.6301 | 3149.41 | 25294.02 | 29001.66 | VPC | 0.56261 | 26.7378 | 519.902 | 8.1267 | 0.89983 | 7.2269 | 0.41078 | 59
Cordele | GA0810001 | Crisp | 12000 | 645.443 | Note 1 | Note 1 | 645.443 | 393.809 | Note 1 | Note 1 | 0.98452 | 394.7935 | 250.6495 | 4.7451 | 245.9043 | 251.634 | 133 | 6315 | 70 | 154700.25 | 3.47 | 239.68 | 42.5862 | 251.634 | 16465.64 | 58938.35 | 75639.96 | VPC | 2.0587 | 106.6842 | 5065.4926 | 11.9405 | 2.6074 | 9.3331 | 5.7743 | 72
Cornelia | GA1370003 | Habersham | 3679 | 1005.946 | Note 1 | 3.51 | 1051.9364 | 934.182 | Note 1 | 0.53 | 2.3355 | 937.0475 | 114.889 | 4.6709 | 110.2181 | 117.7544 | 70.8 | 3005 | 91 | 4222213 | 4.42 | 367.32 | 27.6939 | 117.7544 | 20645.42 | 40485.3 | 62183.26 | VPC | 4.2586 | 100.4883 | 4265.0752 | 20.343 | 6.8704 | 13.4726 | 3.9799 | 67
Covington | GA2170001 | Newton | 17272 | Note 1 | 2358.168 | 1267.279 | 1107.1456 | 1023.849 | Note 1 | Note 1 | 2.5596 | 1026.4086 | 80.737 | 5.1192 | 75.6177 | 83.2966 | 188 | 9212 | 90 | 6283784.9 | 6.14 | 2240 | 78.8032 | 83.2966 | 31432.16 | 169383.66 | 206549.38 | VPC | 1.5225 | 22.4893 | 1101.9776 | 21.7994 | 3.4121 | 18.3873 | 0.95958 | 64
Coweta County Water & Sewerage Authority | GA0770042 | Coweta | 92907 | 1744.3287 | 1549.597 | 356.2025 | 2935.7893 | 2496.685 | Note 1 | 5.1801 | 26.8741 | 2528.7392 | 407.05 | 19.0052 | 388.0448 | 439.1043 | 1142.9 | 35100 | 109 | Note 5 | 7.81 | 2929.75 | 455.4622 | 439.1043 | 148364.95 | 1136874.27 | 1379150.11 | VPC | 1.4835 | 30.2888 | 930.2095 | 36.6165 | 4.2269 | 32.3896 | 0.85198 | 75
Cumming Utilities - City of Cumming, GA | GA1170000 | Forsyth | 66957 | 2910.332 | Note 1 | 398.1624 | 2503.6433 | 2219.0881 | Note 1 | 25.0441 | 3.2925 | 2247.4247 | 256.2186 | 29.1933 | 227.0254 | 284.5552 | 400 | 22637 | 106.32 | Note 5 | 4.25 | 629.536 | 215.7483 | 284.5552 | 123340.22 | 142920.64 | 284099.77 | VPC | 3.5332 | 27.4766 | 1554.9682 | 11.7622 | 5.4486 | 6.3136 | 1.0523 | 73
Cuthbert | GA2430000 | Randolph | 3770 | 425 | Note 1 | Note 1 | 425 | 97.519 | Note 1 | Note 1 | 5.3125 | 102.8315 | 322.1685 | 10.951 | 311.2175 | 327.481 | 20 | 1365 | 56 | 567786 | 3.9 | 383.67 | Note 3 | Note 6 | 42709.03 | 119404.81 | 164152.09 | VPC | 21.9801 | 624.6524 | 42632.5296 | 118.7647 | 31.2887 | 87.4761 | Note 3 | 37.3667
Dade County Water & Swwer Authority | GA0830000 | Dade | 16251 | 821.229 | Note 1 | Note 1 | 837.9888 | 496.572 | Note 1 | Note 1 | 51.263 | 547.835 | 290.1538 | 28.6182 | 261.5355 | 341.4168 | 364 | 8516 | 104 | Note 5 | 4.8 | 712.81 | 123.2425 | 341.4168 | 137367.5 | 186425.15 | 360333.43 | VPC | 9.2069 | 84.1399 | 1968.5048 | 38.0217 | 16.1305 | 21.8912 | 2.1221 | 74
Dahlonega / Dahlonega Water System | GA1870000 | Lumpkin | 7500 | 369.613 | Note 1 | 26.8812 | 337.9758 | 265.484 | Note 1 | Note 1 | 0.66371 | 266.1477 | 71.8281 | 4.0091 | 67.819 | 72.4918 | 70.1 | 2518 | 150 | 2022882.44 | 11.93 | 708.38 | 41.4425 | 72.4918 | 47828.28 | 48041.64 | 96340.08 | VPC | 4.3621 | 73.7909 | 2650.5782 | 38.0738 | 18.9946 | 19.0793 | 1.6365 | 67
Dallas | GA2230000 | Paulding | 14000 | 10.82 | 312.645 | Note 1 | 324.7521 | 209.291 | Note 1 | 0.674 | 0.52323 | 210.4882 | 114.2639 | 1.2551 | 113.0088 | 115.4611 | 43.5 | 3810 | 87.76 | Note 5 | 9.94 | 4790 | 25.8449 | 115.4611 | 12458.26 | 541312.12 | 559505.1 | VPC | 0.90253 | 81.2633 | 7117.5433 | 145.3466 | 3.2699 | 142.0767 | 4.3726 | 88
Dalton Utilities | GA3130000 | Whitfield | 102864 | 8182.368 | 235.5483 | 313.8059 | 7903.5175 | 5529.97 | 30.9348 | Note 1 | 292.94 | 5853.8448 | 2049.6727 | 50.0132 | 1999.6595 | 2342.6127 | 1214.9375 | 37244 | 110.4 | 23488000 | 4.6135 | 1584.73 | 489.9757 | 2342.6127 | 230735.02 | 3168920.37 | 3863886.19 | VPC | 3.6791 | 147.098 | 4509.3012 | 91.2806 | 6.1952 | 85.0854 | 4.0811 | 76
Dawson | GA2730001 | Terrell | 5299 | 433.325 | Note 1 | Note 1 | 541.6562 | 161.734 | Note 1 | Note 1 | 0.40434 | 162.1383 | 379.5179 | 22.8633 | 356.6546 | 379.9223 | 50 | 2038 | 50 | Note 5 | 3.92 | 275.3 | 10.5157 | 379.9223 | 89624.16 | 98187.01 | 187922.49 | VPC | 30.7356 | 479.4583 | 19542.7183 | 92.1546 | 43.9765 | 48.1781 | 33.9166 | 50
Dawsonville | GA0850000 | Dawson | 3866 | 120.609 | Note 1 | Note 1 | 120.609 | 89.8896 | 0.04 | 4.2899 | 0.22482 | 94.4444 | 26.1646 | 2.3717 | 23.7929 | 30.6794 | 25.46 | 1685 | 60 | Note 5 | 22.65 | 626.9 | 8.5517 | 30.6794 | 51790.43 | 14915.79 | 69536.53 | VPC | 3.8562 | 38.6861 | 2560.3354 | 39.5883 | 30.7362 | 8.8521 | 2.7822 | 70
DeKalb County Department of Watershed Management | GA0890001 | DeKalb | 750000 | 22672.15 | Note 1 | 6.667 | 22665.483 | 22000 | Note 1 | 5.77 | 55 | 22060.77 | 604.713 | 110 | 494.713 | 665.483 | 3128 | 221699 | 104 | 64226113 | 3.3 | 320.49 | 1904.7314 | 665.483 | 363000 | 158550.57 | 541026.75 | VPC | 1.3594 | 6.1136 | 433.305 | 2.3525 | 1.6374 | 0.71516 | 0.25973 | 66
Demorest | GA1370004 | Habersham | 18125 | 89.64 | 633.68 | 9.61 | 707.9955 | 481.8 | Note 1 | 5.8 | 1.2045 | 488.8045 | 219.191 | 7.3343 | 211.8568 | 226.1955 | 312 | 6971 | 110 | Note 5 | 8.88 | 1833.81 | 109.7528 | 226.1955 | 64715.36 | 388505.05 | 466065.32 | VPC | 2.8825 | 83.2634 | 1860.3509 | 65.0151 | 9.2835 | 55.7316 | 1.9303 | 51
Douglas | GA0690002 | Coffee | 11255 | 1314.069 | Note 1 | Note 1 | 1301.0584 | 1037.083 | Note 1 | Note 1 | 16.2632 | 1053.3462 | 247.7122 | 60.4287 | 187.2835 | 263.9754 | 125 | 6536 | 65 | 3510387.27 | 3.96 | 234.55 | 39.304 | Note 6 | 239297.53 | 43927.35 | 287039.42 | VPC | 25.3302 | 78.5045 | 4104.8442 | 43.3331 | 36.6122 | 6.7208 | 4.765 | 62.3529
Douglas/Oak Park | GA0690014 | Coffee | 260 | 74.58 | Note 1 | Note 1 | 73.8416 | 47.916 | Note 1 | Note 1 | 0.92302 | 48.839 | 25.0026 | 2.8263 | 22.1763 | 25.9256 | 12 | 597 | 65 | 109995.24 | 4.09 | 482.73 | Note 3 | Note 6 | 11559.52 | 10705.15 | 22710.24 | VPC | 12.9703 | 101.7704 | 5063.0766 | 37.2943 | 19.3627 | 17.9316 | Note 3 | 62.3529
Douglsville-Douglas County Water and Sewer Authority | GA0970000 | Douglas | 145814 | 4547.928 | 17.184 | 30 | 4537.416 | 3829.9641 | Note 1 | 18.647 | 18.356 | 3866.9671 | 670.4489 | 77.7581 | 592.6908 | 707.4519 | 960.87 | 45968 | 97 | 21195064 | 6.39 | 355.55 | 428.1706 | 707.4519 | 495160.77 | 210731.2 | 719048.38 | VPC | 4.6344 | 35.3248 | 1689.9376 | 15.3562 | 10.7719 | 4.5843 | 1.3842 | 81
Dublin | GA1750002 | Laurens | 21362 | 1071.5789 | Note 1 | Note 1 | 1071.5789 | 758.759 | Note 1 | 27.9609 | 1.8969 | 788.6168 | 282.962 | 63.0093 | 219.9528 | 312.8199 | 227 | 8216 | 62 | Note 5 | 5.57 | 378.51 | 55.6804 | 312.8199 | 340035.72 | 83254.32 | 434591.53 | VPC | 21.0112 | 73.3459 | 2654.6709 | 51.5202 | 41.387 | 10.1332 | 3.9503 | 54
East Dublin | GA1750004 | Laurens | 4087 | 138.8 | Note 1 | Note 1 | 138.8806 | 99.667 | Note 1 | 14.7 | 2 | 116.367 | 22.5136 | 2.8324 | 19.6812 | 39.2136 | 40 | 1448 | 65 | Note 5 | 3.52 | 577.77 | 10.2872 | 39.2136 | 9087.22 | 11371.2 | 30107.19 | VPC | 5.359 | 37.2383 | 1348.0271 | 14.1287 | 6.2757 | 7.853 | 1.9132 | 66
East Point Water Treatment Plant | GA1210003 | Fulton | 33712 | 3440.43 | Note 1 | 1032.641 | 2396.7737 | 1793.2387 | Note 1 | Note 1 | 29.9597 | 1823.1983 | 573.5754 | 19.4863 | 554.0891 | 603.5351 | 194 | 11303 | 74 | 4280962 | 3.91 | 241.58 | 74.1422 | Note 6 | 76191.36 | 2166488.41 | 2249917.43 | CRUC | 4.7233 | 134.3053 | 7825.0121 | 198.4146 | 6.7408 | 191.6738 | 7.4733 | 70.9579
Eastman | GA0910002 | Dodge | 7833 | 433.511 | Note 1 | Note 1 | 420.8845 | 243.396 | Note 1 | 3.917 | 5.2611 | 252.5741 | 168.3104 | 2.2805 | 166.0299 | 177.4885 | 65 | 3517 | 61 | 1866237 | 5.06 | 328.63 | 19.5754 | Note 6 | 11539.5 | 840111.18 | 854666.86 | CRUC | 1.7765 | 129.3365 | 6998.0981 | 242.1526 | 3.2811 | 238.8715 | 8.4816 | 54.1137
Eatonton-Putnam Water & Sewer Authority | GA2370000 | Putnam | 11479 | Note 1 | 447.266 | 25.8 | 421.466 | 345 | Note 1 | 14.002 | 0.8625 | 359.8645 | 61.6015 | 9.0516 | 52.5499 | 76.466 | 242 | 14522 | 78 | 3068922 | 3.5 | 446.25 | 99.2897 | 76.466 | 30807.88 | 23450.41 | 60891.56 | VPC | 1.7077 | 9.9141 | 594.9273 | 3.7363 | 2.1215 | 1.6148 | 0.52926 | 78
Effingham County Surface Water System | GA1030131 | Effingham | 7700 | Note 1 | 975.603 | Note 1 | 975.603 | 944.517 | Note 1 | Note 1 | 0.01 | 944.527 | 31.076 | 14.3409 | 16.7351 | 31.086 | 103.21 | 4108 | 45 | 1172824 | 2.74 | 1202.15 | 19.2922 | Note 6 | 39294 | 20118.13 | 59424.15 | VPC | 9.5643 | 11.1611 | 444.2366 | 14.4625 | 9.5652 | 4.8973 | 0.86745 | 55.0222
Elberton | GA1050001 | Elbert | 9000 | 665.909 | Note 1 | 127.407 | 561.3585 | 459.754 | 0.785 | 5.962 | 1.1513 | 467.6523 | 93.7062 | -3.6423 | 97.3485 | 100.8195 | 128.39 | 3979 | 74 | 1405706 | 3.87 | 507.58 | 34.8818 | 100.8195 | 31662.68 | 49412.15 | 84685.42 | VPC | -2.5079 | 67.029 | 2077.3287 | 20.3757 | 7.9574 | 12.4182 | 2.7908 | 65
Ellijay Gilmer County Water & Sewer Authority | GA1230000 | Gilmer | 17188 | 1051 | Note 1 | 72 | 980.2171 | 839 | Note 1 | 58 | 2.0975 | 899.0975 | 81.1196 | 24.0917 | 57.0279 | 141.2171 | 243 | 6875 | 93.8 | 2903886 | 4.75 | 548.54 | 80.3159 | 141.2171 | 109030.12 | 31282.09 | 173278.09 | VPC | 9.6007 | 22.7259 | 642.9664 | 20.409 | 15.8589 | 4.5501 | 0.71005 | 81
Etowah Water & Sewer Authority | GA0850007 | Dawson | 13843 | 659.63 | 1.227 | Note 1 | 664.0697 | 501.931 | Note 1 | 5.435 | 32.339 | 539.705 | 124.3647 | 11.7292 | 112.6354 | 162.1387 | 207.89 | 7633 | 99 | 3987520.62 | 13.61 | 331.48 | 82.0133 | 162.1387 | 158162.07 | 37336.39 | 208019.78 | VPC | 4.21 | 40.4284 | 1484.3916 | 25.6123 | 20.7208 | 4.8914 | 1.3734 | 77
Fairburn | GA1210004 | Fulton | 16453 | Note 1 | 523.972 | Note 1 | 518.7842 | 448.579 | Note 1 | Note 1 | 1.1214 | 449.7004 | 69.0837 | 6.774 | 62.3097 | 70.2052 | 86 | 7110 | 75 | 3479916 | 8.62 | 4950 | 41.9319 | 70.2052 | 58391.85 | 308433.09 | 372376.1 | VPC | 2.6103 | 24.0101 | 1985.018 | 51.5928 | 8.2126 | 43.3802 | 1.486 | 66
Fayette County Water System | GA1130001 | Fayette | 77051 | 3738.499 | 1.4234 | 309.728 | 3549.3181 | 2977.397 | 0.559 | 1.498 | 7.4449 | 2986.8989 | 562.4192 | 75.6836 | 486.7357 | 571.3621 | 720.76 | 32836 | 87.7 | 15240653 | 6.44 | 540.52 | 282.4834 | 571.3621 | 487221.74 | 263090.37 | 755145.92 | VPC | 6.3148 | 40.6116 | 1850.1615 | 22.8503 | 14.838 | 8.0123 | 1.7231 | 72
Fayettville | GA1130003 | Fayettville | 18645 | 308.1799 | 307.888 | Note 1 | 616.4691 | 476.7367 | Note 1 | Note 1 | 1.1918 | 477.9285 | 138.5406 | 7.1992 | 131.3414 | 139.7324 | 101.4 | 7932 | 60 | Note 5 | 4.07 | 1361.29 | 38.0704 | 139.7324 | 29300.76 | 178793.72 | 209716.93 | VPC | 2.4866 | 45.3655 | 3548.7122 | 26.2348 | 3.694 | 22.5408 | 3.45 | 68
Fitzgerald Utilities | GA0170000 | Ben Hill | 9050 | 925.661 | Note 1 | Note 1 | 898.7 | 669.708 | Note 1 | 10.007 | 11.2338 | 690.9487 | 207.7513 | 14.3421 | 193.4092 | 228.992 | 132 | 6059 | 60.58 | 1214738.04 | 2.09 | 104.08 | 35.8866 | Note 6 | 29974.94 | 20130.03 | 52315.71 | VPC | 6.4851 | 87.4547 | 4014.3042 | 8.2695 | 4.9472 | 3.3223 | 5.3895 | 62.6844
Flowery Branch | GA1390000 | Towns | 4254 | 127.664 | 1.149 | Note 1 | 128.813 | 118.325 | Note 1 | Note 1 | 0.29581 | 118.6208 | 10.1922 | 4.5032 | 5.689 | 10.488 | 21 | 7934 | 80 | 997035 | 6.82 | 744.35 | 38.0683 | 10.488 | 41055.69 | 4234.6 | 45510.48 | VPC | 1.555 | 1.9645 | 742.2038 | 5.7084 | 5.1747 | 0.53373 | 0.14944 | 52
Floyd County | GA1150001 | Floyd | 99038 | 1449.312 | 646.122 | 0.101 | 2138.0949 | 1504.062 | Note 1 | 10.337 | 1 | 1515.399 | 622.6959 | 87.2255 | 535.4704 | 634.0329 | 592 | 19216 | 90 | 6519606 | 4.9 | 575.306 | 199.8962 | 634.0329 | 425052.19 | 308059.32 | 739633.75 | VPC | 12.4362 | 76.3448 | 2478.1117 | 38.1511 | 22.1197 | 16.0314 | 2.6787 | 72
Folkston | GA0490000 | Charlton | 3300 | 173.183 | Note 1 | 1.609 | 169.3231 | 146.762 | Note 1 | 0.168 | 0.3669 | 147.2969 | 22.0262 | 2.218 | 19.8083 | 22.5611 | 61.2 | 2412 | 52 | 547048 | 3.09 | 316.59 | 13.1511 | 22.5611 | 6848.76 | 6271.1 | 13289.21 | VPC | 2.5193 | 22.4997 | 886.7516 | 5.4394 | 2.8395 | 2.6 | 1.5062 | 48
Forsyth County Department of Water and Sewer | GA1170050 | Forsyth | 204505 | 5677.005 | 429.499 | 50.485 | 5639.149 | 5080.634 | Note 1 | 15.604 | 12.7016 | 5108.9396 | 530.2094 | 129.408 | 400.8014 | 558.515 | 1120.3 | 67140 | 116.6 | 44911416.6 | 11.09 | 1466.54 | 686.5543 | 558.515 | 1432070.44 | 587791.3 | 2061373.01 | VPC | 5.2806 | 16.3552 | 980.1714 | 30.0843 | 21.3296 | 8.7547 | 0.58379 | 72
Forsyth/Water Department | GA2070001 | Monroe | 8918 | 517.619 | 17.318 | 19.881 | 542.2722 | 512.669 | Note 1 | Note 1 | 2.3 | 514.969 | 27.3032 | 5.2136 | 22.0897 | 29.6032 | 51 | 3430 | 70 | 1893591.61 | 7.87 | 626.6 | 20.195 | Note 6 | 41030.87 | 13841.39 | 56313.44 | VPC | 4.1644 | 17.6442 | 1186.6597 | 15.9977 | 11.9624 | 4.0354 | 1.0938 | 75.7103
Fort Oglethorpe | GA0470001 | Catoosa | 7909 | Note 1 | 289.172 | Note 1 | 289.172 | 190.661 | Note 1 | Note 1 | 3.6147 | 194.2757 | 94.8964 | 1.1996 | 93.6968 | 98.511 | 38 | 3055 | 110 | 1426364 | 8.35 | 1826.96 | 26.6528 | Note 6 | 10016.51 | 782368.01 | 798988.34 | CRUC | 1.0758 | 84.0273 | 6755.3545 | 259.373 | 3.2787 | 256.0943 | 3.5155 | 75.5889
Fort Valley Utility Commission | GA2250001 | Peach | 11855 | 645.49 | Note 1 | Note 1 | 652.0101 | 478.91 | Note 1 | Note 1 | 8.1501 | 487.0601 | 164.95 | 17.6389 | 147.311 | 173.1001 | 157 | 5514 | 55 | 3035830 | 6.34 | 376.44 | 33.6551 | Note 6 | 111768.47 | 55453.76 | 170290.26 | VPC | 8.7642 | 73.194 | 2570.6487 | 30.3268 | 20.2699 | 10.0569 | 4.3771 | 62.8529
Franklin County | GA1190051 | Flanklin | 5691 | 446.2538 | 372.5713 | 190.4146 | 628.4105 | 474.7643 | Note 1 | 5.728 | 1.1869 | 481.6792 | 146.7312 | 17.2344 | 129.4968 | 153.6462 | 244 | 2508 | 125 | 2888396 | 5.91 | 1911.48 | 77.391 | 153.6462 | 101147 | 247530.62 | 361895.33 | VPC | 18.8268 | 141.4617 | 1454.0404 | 139.0262 | 40.3297 | 98.6964 | 1.6733 | 55
Gainesville-Department of Water Resources | GA1390001 | Hall | 171109 | 7349.17 | Note 1 | Note 1 | 7344.392 | 6746.739 | Note 1 | 51.8867 | 121.142 | 6919.7677 | 424.6243 | 230.9563 | 193.668 | 597.653 | 1460 | 61897 | 129 | 34786086 | 5.56 | 359.82 | 809.0686 | 597.653 | 1275743.19 | 69685.63 | 1407688.01 | VPC | 10.2227 | 8.5723 | 363.4229 | 21.7366 | 20.6107 | 1.1258 | 0.23937 | 79
Garden City | GA0510000 | Chatham | 10306 | 371.672 | Note 1 | Note 1 | 358.94 | 270.192 | Note 1 | 16.889 | 1.851 | 288.932 | 70.008 | 7.2098 | 62.7982 | 88.748 | 51 | 3600 | 52 | Note 5 | 2.63 | 193.52 | 15.486 | 88.748 | 18121.87 | 12152.72 | 33901.15 | VPC | 5.4869 | 47.7917 | 3373.5291 | 8.4096 | 5.0339 | 3.3758 | 4.0552 | 48
Glen of Robin Hood | GA0510109 | Chatham | 6572 | 213.088 | Note 1 | Note 1 | 213.088 | 177.682 | Note 1 | Note 1 | 0.4442 | 178.1262 | 34.9618 | 0.88841 | 34.0734 | 35.406 | 37 | 2434 | 45 | Note 5 | 2.33 | 208.47 | 9.2846 | 35.406 | 2070 | 7103.28 | 9265.88 | VPC | 1 | 38.3532 | 2523.02 | 3.7688 | 0.85045 | 2.9184 | 3.6699 | 46
Glennville | GA2670002 | Tattnal | 5300 | 260.56 | Note 1 | Note 1 | 264.1793 | 205.212 | Note 1 | 4.109 | 0.51303 | 209.834 | 54.3452 | 3.1404 | 51.2048 | 58.9673 | 52 | 2129 | 46.8 | 584460 | 4.56 | 251.53 | 10.2606 | 58.9673 | 14141.46 | 12879.55 | 28183.59 | VPC | 4.0413 | 65.8935 | 2697.8299 | 12.6919 | 6.6423 | 6.0496 | 4.9904 | 68
Gray | GA1690000 | Jones | 5170 | 114.1472 | 103.799 | 2.913 | 215.5031 | 179.571 | Note 1 | 1.0842 | 0.44893 | 181.1041 | 34.399 | 3.6489 | 30.75 | 35.9321 | 60.6 | 2032 | 60 | 945469.37 | 6.79 | 2120.78 | 13.8549 | 35.9321 | 24699.28 | 65214.08 | 93164.8 | VPC | 4.9198 | 41.46 | 1390.2095 | 44.2487 | 12.1552 | 32.0935 | 2.2194 | 49
Griffin | GA2550000 | Spalding | 23643 | 3073.4 | Note 1 | 2003.685 | 945.173 | 737.177 | Note 1 | 41.574 | 9.8694 | 788.6203 | 156.5527 | 10.9963 | 145.5564 | 207.996 | 212.7 | 11697 | 77.2 | Note 5 | 9.28 | 441.35 | 81.8643 | 207.996 | 98595.81 | 64241.32 | 185541.66 | VPC | 2.5756 | 34.0929 | 1874.8692 | 13.9213 | 8.4292 | 5.4921 | 1.778 | 82
Grovetown | GA0730001 | Columbia | 14777 | 9.3975 | 407.7819 | Note 1 | 417.5006 | 364.6213 | Note 1 | 0.10809 | 0.91155 | 365.6409 | 51.8597 | 1.8231 | 50.0366 | 52.8794 | 69.2 | 5622 | 80 | 3495930.96 | 6.8972 | 2017.9213 | 35.556 | 52.8794 | 12574.41 | 100969.95 | 115601.92 | VPC | 0.88844 | 24.384 | 1981.0204 | 20.1964 | 2.2366 | 17.9598 | 1.4073 | 48
Gwinnett County Department of Water Resources / Lawrenceville | GA135004 / GA1350005 | Gwinnett | 987112 | 28699.045 | Note 1 | 104.958 | 28112.0415 | 25250.1 | Note 1 | 2.65 | 9.168 | 25261.918 | 2850.1235 | 466.9173 | 2383.2062 | 2861.9415 | 4023.2 | 285235 | 112 | 26231016 | 5.91 | 351.42 | 2638.8352 | 2861.9415 | 2759246.05 | 837506.33 | 3600905.46 | VPC | 4.4848 | 22.8911 | 1622.9201 | 12.6098 | 9.6736 | 2.9362 | 0.90313 | 82
Hahira | GA1850000 | Lowndes | 3562 | 93.436 | Note 1 | Note 1 | 98.3537 | 103.821 | Note 1 | 2.728 | 1.2294 | 107.7784 | -9.4247 | 2.128 | -11.5527 | -5.4673 | 25 | 2961 | 60 | 409517 | 5.88 | 1495.91 | 12.6889 | Note 6 | 12512.7 | -17281.87 | 1150.78 | VPC | 1.969 | -10.6894 | -1266.0545 | -1.6107 | 4.2258 | -5.8365 | -0.91046 | 59.9706
Hampton GA | GA1510000 | Henry | 8323 | 19.735 | 238.734 | Note 1 | 260.37 | 162.2743 | Note 1 | Note 1 | 0.40569 | 162.68 | 97.6901 | 9.3521 | 88.3379 | 98.0957 | 42.5 | 2641 | 54 | Note 5 | 11.7502 | 3788.4447 | 12.3399 | 98.0957 | 109889.5 | 334663.41 | 446089.82 | VPC | 9.7017 | 91.6402 | 5694.6296 | 168.3275 | 41.609 | 126.7184 | 7.1587 | 62
Hapeville Water Department | GA1210006 | Fulton | 6500 | Note 1 | 290.435 | Note 1 | 292.2469 | 246.425 | Note 1 | 3.634 | 0.61606 | 250.6751 | 41.5719 | 6.3354 | 35.2365 | 45.8219 | 41 | 2489 | 77.5 | 4986314.75 | 12.14 | 5216.93 | 16.8356 | 45.8219 | 76397.95 | 183826.35 | 282396.58 | VPC | 6.9736 | 38.786 | 2354.594 | 104.5497 | 30.6942 | 73.8555 | 2.093 | 65
Haralson County Water Authority | GA1430007 | Haralson | 11000 | 868.1617 | 72.043 | 511.4616 | 437.493 | 278.3106 | Note 1 | 0.66946 | 0.69578 | 279.6758 | 157.8172 | 1.4474 | 156.3698 | 159.1824 | 396 | 5682 | 89.6 | 3335251 | 6.78 | 510.33 | 97.9374 | 159.1824 | 9812.26 | 79800.2 | 90309.19 | VPC | 0.69788 | 75.3978 | 1081.8445 | 15.7713 | 1.7269 | 14.0444 | 1.5966 | 68
Harris County Waterworks | GA1450011 | Harris | 23782 | 664.75 | 355.403 | 1.62 | 1012.6769 | 878.696 | Note 1 | 0.0756 | 2.1967 | 880.9683 | 131.7086 | 26.9261 | 104.7825 | 133.9809 | 521 | 9405 | 90.2 | 5581076.14 | 5.93 | 1684.26 | 139.2432 | 133.9809 | 159663.45 | 176480.92 | 339971.59 | VPC | 7.8437 | 30.5237 | 551.0082 | 35.741 | 16.9764 | 18.7646 | 0.75251 | 53
Hart County Water and Sewer Authority | GA1470065 | Hart | 5317 | Note 1 | 391.749 | 25.304 | 366.2418 | 318.241 | Note 1 | 3.2679 | 0.7956 | 322.3045 | 43.9373 | 2.2678 | 41.6695 | 48.0008 | 181.41 | 2966 | 95 | 2491206.69 | 5.32 | 1987.56 | 49.4579 | 48.0008 | 12041.75 | 82820.59 | 102938.76 | VPC | 2.0948 | 38.4905 | 629.309 | 31.9833 | 4.0599 | 27.9233 | 0.84252 | 61
Hartwell | CS1470000 | Hart | 7116 | 691.844 | Note 1 | 194.6046 | 486.3229 | 427.0258 | Note 1 | 18.7751 | 2.3098 | 448.1107 | 38.2122 | 18.0676 | 20.1446 | 59.2971 | 89.2237 | 3061 | 86.57 | 1976882.42 | 5.17 | 408.09 | 29.7606 | Note 6 | 93409.47 | 8220.79 | 110234.8 | VPC | 16.1713 | 18.0302 | 618.5641 | 33.2017 | 30.516 | 2.6857 | 0.67689 | 65.5436
Hawkinsville | GA2350001 | Pulaski | 6650 | 290.074 | Note 1 | Note 1 | 290.074 | 204.287 | Note 1 | 8.634 | 0.51072 | 213.4317 | 76.6423 | 1.0214 | 75.6208 | 85.787 | 60 | 1847 | 55 | 948027.67 | 4.1 | 2843.27 | 12.0781 | 85.787 | 4187.88 | 215010.49 | 245199.27 | VPC | 1.5151 | 112.1713 | 3453.0067 | 118.6781 | 2.2674 | 116.4107 | 6.261 | 41
Hazlehurst | GA1610001 | Jeff Davis | 8058 | 310.632 | Note 1 | Note 1 | 326.2941 | 181.461 | 8.923 | 4.586 | 0.47596 | 195.446 | 130.8482 | 10.7439 | 120.1043 | 135.9101 | 78 | 4596 | 51 | Note 5 | 2.68 | 265.48 | 20.6883 | 135.9101 | 28210.78 | 31885.29 | 61439.91 | VPC | 6.4045 | 71.5955 | 4218.6263 | 13.0757 | 6.1381 | 6.9376 | 5.8054 | 72
Heard County Water Authority | GA1490000 | Heard | 8172 | 546.86 | 2.82 | 64.301 | 486.4324 | 238.559 | Note 1 | 7.3175 | 0.5964 | 246.4729 | 239.9595 | 14.1337 | 225.8258 | 247.8734 | 400 | 3983 | 80 | Note 5 | 11.2901 | 831.1874 | 80.6343 | 247.8734 | 155542.07 | 187703.59 | 349823.57 | VPC | 9.7219 | 155.3354 | 1546.7523 | 86.1777 | 39.0515 | 47.1262 | 2.8006 | 60
Henry County Water Authority | GA1510001 | Henry | 250000 | 6594.873 | 0.75008 | 655.0942 | 5970.8399 | 5240.0833 | Note 1 | 127.5861 | 19.1514 | 5386.8208 | 584.0191 | 83.4412 | 500.5779 | 730.7566 | 1377.058 | 72982 | 99 | 38121771 | 8.6452 | 376.06 | 664.7822 | 730.7566 | 708213.72 | 188247.31 | 951643.13 | VPC | 3.1324 | 18.7916 | 995.9248 | 12.2833 | 9.704 | 2.5794 | 0.753 | 89
Hephzibah Waterworks | GA2450002 | Richmond | 3830 | 235.404 | Note 1 | Note 1 | 235.404 | 178.777 | Note 1 | 1.408 | 0.44694 | 180.6319 | 54.7721 | 7.9141 | 46.858 | 56.627 | 50.4 | 1802 | 70 | Note 5 | 2.89 | 753.86 | 13.8727 | 56.627 | 22754.51 | 35324.36 | 59477.23 | VPC | 12.0324 | 71.242 | 2547.183 | 32.2302 | 12.6274 | 19.6029 | 3.3777 | 66
Hiawassee | GA2810000 | Towns | 6442 | 485.11 | Note 1 | 266.609 | 194.4028 | 112.766 | Note 1 | 2.5364 | 0.28192 | 115.5843 | 78.8185 | 3.5203 | 75.2982 | 81.6368 | 75.4 | 2453 | 95 | Note 5 | 3.41 | 1179.11 | 26.9031 | 81.6368 | 11859.14 | 88784.9 | 103967.09 | VPC | 3.9318 | 84.0997 | 2736.0282 | 41.029 | 4.8345 | 36.1944 | 2.7989 | 71
Hinesville | GA1790000 | Liberty | 24666 | 1338.293 | Note 1 | Note 1 | 1325.0426 | 1097.614 | 0.963 | 19.192 | 16.563 | 1134.332 | 190.7105 | 8.8557 | 181.8549 | 226.4656 | 210.05 | 14762 | 52 | 2418931 | 5.1 | 134.06 | 63.5957 | Note 6 | 45163.84 | 24379.47 | 74336.63 | VPC | 1.6435 | 33.751 | 2371.9713 | 4.711 | 3.0595 | 1.6515 | 2.8595 | 85.9495
Hogansville | GA2850000 | Troup | 3866 | Note 1 | 161.225 | Note 1 | 160.4229 | 101.518 | Note 1 | Note 1 | 2.0053 | 103.5233 | 56.8996 | 5.4384 | 51.4612 | 58.9049 | 31.3 | 1950 | 100 | 1065854 | 7.98 | 3345.52 | Note 3 | Note 6 | 43398.61 | 172164.4 | 222271.73 | VPC | 7.6409 | 72.3023 | 4504.4577 | 110.5451 | 22.2557 | 88.2894 | Note 3 | 70.7003
Homerville | GA0650000 | Clinch | 3260 | 168.961 | Note 1 | Note 1 | 168.961 | 85.302 | Note 1 | 1.252 | 2.112 | 88.666 | 80.295 | 1.5099 | 78.785 | 83.659 | 45 | 1375 | 45 | 492402.71 | 2.76 | 478.26 | Note 3 | Note 6 | 4167.44 | 37679.74 | 43456.05 | VPC | 3.0086 | 156.9814 | 4796.6543 | 30.4343 | 3.0309 | 27.4034 | Note 3 | 60.1961
Hoschton | GA1570002 | Jackson | 1877 | 37.307 | 90.021 | Note 1 | 127.8007 | 89.965 | Note 1 | 2.801 | 0.22491 | 92.9909 | 34.8097 | 0.64504 | 34.1647 | 37.8357 | 30.6 | 2025 | 38 | Note 5 | 12.45 | 2311.89 | 6.5091 | 37.8357 | 7971.03 | 78985.03 | 93951.64 | VPC | 0.87271 | 46.2232 | 3058.8862 | 42.9413 | 3.9363 | 39.005 | 5.2487 | 65
Houston County - Feagin Mill System | GA1530021 | Houston | 163000 | 5984.458 | Note 1 | 2067.705 | 3761.177 | 2749.554 | 28 | 0.6 | 6.9439 | 2785.0979 | 976.0791 | 41.6671 | 934.412 | 983.623 | 500 | 19405 | 65 | Note 5 | 2.77 | 307.19 | 133.2337 | 983.623 | 115402.95 | 287042.03 | 404762.38 | VPC | 5.8828 | 131.9265 | 5120.0658 | 20.7392 | 5.9471 | 14.7922 | 7.0133 | 57
Jackson County Water and Sewerage Utility | GA1570117 | Jackson | 34194 | Note 1 | 1496.604 | 483.733 | 1014.414 | 731.193 | Note 1 | 217.907 | 12.6802 | 961.7802 | 52.6338 | 8.3671 | 44.2668 | 283.221 | 449.4 | 15604 | 102 | 10530.4 | 8.72 | 2286.04 | 177.6561 | Note 6 | 72969.05 | 101195.64 | 701296.2 | VPC | 1.4691 | 7.7723 | 269.8684 | 11.1615 | 4.6763 | 6.4852 | 0.24917 | 74.3768
Jasper | GA2270000 | Pickens | 13548 | 519.76 | 237.6715 | 23.021 | 749.1081 | 398.2986 | Note 1 | 10.8602 | 0.99575 | 410.1545 | 338.9536 | 6.1244 | 332.8291 | 350.8095 | 200 | 6088 | 70 | 3907746 | 3.55 | 1071.71 | 50.9774 | 350.8095 | 21469.79 | 356696.33 | 390872.23 | VPC | 2.7561 | 149.78 | 4559.3034 | 62.1166 | 3.5266 | 58.5901 | 6.529 | 63
Jefferson | GA1570003 | Jackson | 12355 | 549.603 | 52.239 | Note 1 | 596.4893 | 478 | 0.062 | 18.249 | 10.616 | 506.927 | 89.5623 | 9.9474 | 79.6149 | 118.4273 | 129.77 | 5638 | 85 | Note 5 | 8.56 | 924.16 | 48.0191 | 118.4273 | 83027.73 | 73576.95 | 183280.55 | VPC | 4.8338 | 38.688 | 1680.844 | 27.7766 | 14.7265 | 13.0502 | 1.658 | 70
Jesup Water System | GA3050000 | Wayne | 9952 | 462.866 | Note 1 | Note 1 | 474.068 | 404.77 | Note 1 | Note 1 | 1.0119 | 405.7819 | 68.2861 | 10.2845 | 58.0016 | 69.298 | 136 | 5075 | 57.5 | 949197 | 8.34 | 259.91 | 31.4185 | 69.298 | 85772.42 | 15075.2 | 101110.62 | VPC | 5.552 | 31.312 | 1168.4451 | 19.8715 | 16.901 | 2.9705 | 1.8461 | 73
Jones County Water System | GA1690002 | Jones | 13500 | 559.2927 | Note 1 | 103.499 | 469.8905 | 405.7365 | Note 1 | Note 1 | 1.0143 | 406.7509 | 63.1396 | 2.0287 | 61.1109 | 64.1539 | 140.2 | 4835 | 77 | Note 5 | 3.76 | 718.87 | 41.7003 | 64.1539 | 7627.85 | 43930.81 | 52287.83 | VPC | 1.1495 | 34.6282 | 1194.2024 | 10.6636 | 1.5776 | 9.086 | 1.4655 | 63
Kingsland | GA0390000 | Camden | 21643 | 681.103 | Note 1 | Note 1 | 698.5672 | 616.7313 | Note 1 | 0.084 | 1.5418 | 618.3571 | 80.2101 | 4.6296 | 75.5805 | 81.8359 | 189.93 | 8781 | 65 | 1476709 | 2.27 | 181.09 | 55.6273 | 81.8359 | 10508.66 | 13686.88 | 24489.96 | VPC | 1.4445 | 23.5816 | 1090.2433 | 2.7554 | 1.1967 | 1.5587 | 1.3587 | 77
Lafayette | GA2950002 | Walker | 16000 | 747.796 | 405.07 | Note 1 | 1142.2271 | 655.832 | Note 1 | 2.971 | 7.2 | 666.003 | 476.2241 | 43.197 | 433.027 | 486.3951 | 638 | 8293 | 75 | Note 5 | 3.02 | 180.2 | 128.5401 | 486.3951 | 130448.32 | 78031.47 | 210312.6 | VPC | 14.2708 | 143.0574 | 1859.5226 | 25.1392 | 15.7299 | 9.4093 | 3.3688 | 66
LaGrange | GA2850001 | Troup | 45688 | 2633.78 | Note 1 | 158.2309 | 2475.5491 | 2040.99 | Note 1 | Note 1 | 5.1025 | 2046.0925 | 429.4566 | 10.205 | 419.2517 | 434.5591 | 466.71 | 20204 | 81 | Note 5 | 5.63 | 454.46 | 164.2484 | 434.5591 | 57453.87 | 190533.12 | 250305.86 | VPC | 1.3838 | 56.8518 | 2461.1316 | 12.2742 | 2.8437 | 9.4305 | 2.5525 | 71
Lake Blackshear Area Water System | GA0810064 | Crisp | 4483 | 102.045 | Note 1 | Note 1 | 102.045 | 81.098 | Note 1 | 3.45 | 0.20275 | 84.7507 | 17.2943 | 0.40549 | 16.8888 | 20.947 | 112 | 1724 | 62 | 656975 | 3 | 251.41 | 19.5641 | 20.947 | 1216.47 | 4246 | 6380.81 | VPC | 0.64439 | 26.8391 | 413.1303 | 3.1685 | 0.70561 | 2.4629 | 0.86325 | 79
Larchmont Utilities | GA0510034 | Chatham | 16339 | 577.275 | Note 1 | Note 1 | 577.275 | 427.264 | Note 1 | 3.416 | 1.0682 | 431.7482 | 145.5268 | 49.9897 | 95.5372 | 150.011 | 62 | 6284 | 52 | 2135969 | 4.98 | 149.7 | 24.2568 | 150.011 | 247115.11 | 14301.92 | 262088.3 | VPC | 21.7947 | 41.6527 | 4221.7051 | 41.6004 | 39.3245 | 2.2759 | 3.9386 | 55
Lavonia | GA1190003 | Franklin | 8190 | 491.26 | 25.304 | 176.527 | 339.5478 | 217.231 | Note 1 | 10.739 | 4.2443 | 232.2143 | 107.3334 | 3.6947 | 103.6388 | 122.3168 | 127 | 3894 | 107 | 1851906 | 4.12 | 462.22 | 49.6455 | Note 6 | 15222.06 | 47903.9 | 70051.56 | VPC | 2.5995 | 72.9178 | 2235.7621 | 16.2111 | 3.9091 | 12.302 | 2.0876 | 65.6565
Lee County Utilities Authority | GA1770068 | Lee | 18468 | 613.551 | Note 1 | Note 1 | 636.8006 | 571.037 | Note 1 | 1.294 | 1.4276 | 573.7586 | 63.042 | 14.5354 | 48.5066 | 65.7636 | 89 | 6840 | 68 | 2310000 | 2.25 | 291.74 | 37.4159 | 65.7636 | 32652.96 | 14151.31 | 47598.27 | VPC | 5.8221 | 19.4291 | 1493.1996 | 6.8427 | 4.7738 | 2.0689 | 1.2964 | 67
Leesburg | GA1770000 | Lee | 3300 | 198.848 | Note 1 | Note 1 | 194.9108 | 165.437 | Note 1 | 25.295 | 0.055 | 190.787 | 4.1238 | 0.82719 | 3.2966 | 29.4738 | 25.3 | 1537 | 62 | Note 5 | 2.75 | 152.41 | 8.3148 | 29.4738 | 2274.76 | 502.44 | 6640.79 | VPC | 1.4745 | 5.8763 | 356.9892 | 1.8069 | 1.48 | 0.32689 | 0.39648 | 87
Lincoln County BOC | GA1810038 | Lincoln | 6093 | 37.343 | 99.414 | Note 1 | 137.2825 | 72.175 | Note 1 | Note 1 | 0.18044 | 72.3554 | 64.9271 | 1.0163 | 63.9108 | 65.1075 | 140.7 | 2395 | 75.5 | Note 5 | 16.17 | 1796.88 | 30.8764 | 65.1075 | 16434.37 | 114839.97 | 131598.56 | VPC | 1.1626 | 73.1098 | 1244.4774 | 54.8118 | 6.8619 | 47.9499 | 2.0699 | 64
Locust Grove | GA1510002 | Henry | 9750 | 155.461 | 116.422 | Note 1 | 273.8714 | 250.803 | Note 1 | 13.456 | 3.4234 | 267.6824 | 6.189 | 3.3086 | 2.8804 | 23.0684 | 49.5 | 4035 | 60 | 2151404 | 8.57 | 1215.87 | 19.1197 | Note 6 | 28354.75 | 3502.21 | 52380.11 | VPC | 2.2465 | 1.9558 | 159.4254 | 7.8952 | 7.0272 | 0.86796 | 0.15065 | 65.726
Loganville | GA1350006 | Walton | 12319 | Note 1 | 482.544 | Note 1 | 478.9519 | 331.102 | Note 1 | 8.612 | 0.82775 | 340.5418 | 138.4101 | 6.8288 | 131.5813 | 147.8499 | 88.5 | 5719 | 80 | Note 5 | 0.44 | 3072 | 39.0297 | 147.8499 | 70326.58 | 404217.71 | 503543.22 | VPC | 3.2714 | 63.0349 | 4073.4088 | 82.9768 | 12.297 | 70.6798 | 3.3713 | 68
Louisville | GA1630002 | Jefferson | 2729 | 457.5064 | Note 1 | Note 1 | 456.4684 | 320.5527 | 0.504 | 9.4534 | 1 | 331.5101 | 124.9583 | 1.6053 | 123.353 | 135.4117 | 40.5 | 1495 | 47.6637 | 665503.68 | 2.8447 | 327.9787 | 7.7132 | 135.4117 | 4566.61 | 40457.18 | 48452.27 | VPC | 2.9418 | 226.0559 | 8344.5322 | 30.1162 | 3.0546 | 27.0617 | 15.9926 | 63
Lowndes Co.-North Lowndes Co. WS | GA1850016 | Lowndes | 7194 | 513.259 | Note 1 | Note 1 | 513.259 | 487.756 | 0.125 | Note 1 | 1 | 488.881 | 24.378 | 2.5025 | 21.8755 | 25.378 | 118 | 6253 | 61 | 2960986 | 6.15 | 267.4 | 35.097 | Note 6 | 15390.61 | 5849.5 | 21507.51 | VPC | 1.0965 | 9.5846 | 507.9049 | 3.3968 | 2.4613 | 0.93547 | 0.62329 | 69.3529
Lowndes Co.-South Lowndes Co. WS | GA1850019 | Lowndes | 7090 | 392.292 | Note 1 | Note 1 | 392.292 | 305.881 | 0.241 | 5.761 | 1 | 312.883 | 79.409 | 1.7454 | 77.6636 | 86.17 | 92 | 3704 | 61 | 1825941 | 6.15 | 351.25 | 23.4522 | Note 6 | 10734.41 | 477630.94 | 490740.15 | CRUC | 1.291 | 57.4452 | 2312.7924 | 131.8481 | 2.8981 | 128.95 | 3.3116 | 69.6078
Lyons | GA2790000 | Toombs | 4476 | 374.688 | Note 1 | Note 1 | 391.3191 | 238.754 | 0.787 | 34.612 | 4.8915 | 279.0445 | 112.2746 | 10.0298 | 102.2448 | 151.7781 | 42 | 2287 | 58 | 797730.28 | 2.92 | 296.99 | 12.0726 | Note 6 | 29287.02 | 30365.67 | 71384.83 | VPC | 12.0153 | 122.4848 | 6669.5871 | 26.0834 | 12.8059 | 13.2775 | 8.4691 | 79.0298
Macon Water Authority | GA0210001 | Bibb | 135000 | 9851.12 | Note 1 | 325.57 | 9131.51 | 7723.71 | Note 1 | 197.75 | 43.81 | 7965.27 | 1166.24 | 178.4163 | 987.8237 | 1407.8 | 1411.99 | 58507 | 121.6 | 18650864 | 5.23 | 870.79 | 728.5596 | 1407.8 | 1222494.95 | 860187.02 | 2293030 | VPC | 8.3548 | 46.2571 | 1916.7036 | 35.5971 | 20.8948 | 14.7023 | 1.3559 | 84
Madison | GA2110002 | Morgan | 5215 | 457.883 | Note 1 | 0.243 | 444.2999 | 354.234 | Note 1 | 13.683 | 5.5537 | 373.4707 | 70.8292 | 11.4301 | 59.399 | 90.0659 | 75 | 3355 | 60 | 3730614 | 6.3 | 561.89 | 19.9071 | Note 6 | 72009.66 | 33375.73 | 116194.33 | VPC | 9.3339 | 48.5058 | 2169.8283 | 31.4114 | 21.4634 | 9.9481 | 2.9838 | 76.0438
Madison County Water System | GA1950060 | Madison | 3078 | 103.7951 | 261.0262 | 9.4061 | 355.4152 | 340.2942 | Note 1 | Note 1 | 0.85074 | 341.1449 | 14.2703 | 6.8836 | 7.3867 | 15.1211 | 103 | 1639 | 65 | Note 5 | 6.5 | 2188.5161 | 19.0531 | 15.1211 | 44743.5 | 16165.98 | 62771.33 | VPC | 11.5065 | 12.3475 | 196.4818 | 37.1626 | 27.2993 | 9.8633 | 0.38769 | 63
Manchester Water Works | GA1990003 | Meriwether | 3997 | 544.5 | Note 1 | 26.8 | 517.7 | 439.037 | Note 1 | 2.5 | 6.4713 | 448.0082 | 69.6918 | 50.907 | 18.7847 | 78.663 | 113 | 2359 | 66 | 2290565 | 5.22 | 590.1 | 23.2512 | Note 6 | 265734.58 | 11084.88 | 282113.39 | VPC | 59.123 | 21.8165 | 455.4429 | 117.3461 | 112.6471 | 4.699 | 0.8079 | 93.6275
Marietta Water/BLW | GA0670005 | Cobb | 60100 | Note 1 | 2782.591 | Note 1 | 2781.7565 | 2519.522 | Note 1 | Note 1 | 34.772 | 2554.294 | 227.4625 | 26.9325 | 200.53 | 262.2345 | 315.8 | 20127 | 86 | 17724903 | 7.32 | 2928.13 | 148.3971 | Note 6 | 197145.78 | 587178.01 | 886140.6 | VPC | 3.6661 | 27.2965 | 1739.7003 | 38.9687 | 9.7951 | 29.1736 | 1.3513 | 79.8847
Marion County | GA1970003 | Marion | 5512 | 364.1577 | Note 1 | Note 1 | 380.9579 | 105.9931 | Note 1 | 0.08945 | 0.26498 | 106.3476 | 274.6104 | 2.6949 | 271.9154 | 274.9648 | 360 | 2674 | 62 | Note 5 | 2.35 | 553.07 | 53.1511 | 274.9648 | 6329.77 | 150388.28 | 156914.08 | VPC | 2.7612 | 278.599 | 2069.3717 | 58.6081 | 2.3672 | 56.2409 | 5.1159 | 58
McCaysville | GA1110001 | Fannin | 8307 | 240.54 | Note 1 | Note 1 | 238.5529 | 121.407 | Note 1 | 1.253 | 0.30352 | 122.9635 | 115.5893 | 1.846 | 113.7433 | 117.1459 | 153 | 3620 | 89 | 1251380.13 | 7.07 | 946.05 | 44.5282 | 117.1459 | 12973.89 | 107606.86 | 122053.29 | VPC | 1.3971 | 86.0844 | 2036.7681 | 33.3096 | 3.5839 | 29.7257 | 2.5544 | 67
McDonough | GA1510003 | Henry | 15608 | 419.97 | 0.19997 | Note 1 | 420.1718 | 318.396 | Note 1 | Note 1 | 0.79599 | 319.192 | 100.9798 | 7.2632 | 93.7166 | 101.7758 | 90 | 5133 | 64.09 | 2795559 | 6.06 | 644.56 | 29.4013 | 101.7758 | 44014.72 | 60405.98 | 104933.77 | VPC | 3.8767 | 50.021 | 2852.865 | 20.343 | 8.5749 | 11.7682 | 3.1875 | 77
McRae Water System | GA2710003 | Telfair | 5903 | 240.37 | Note 1 | Note 1 | 240.37 | 229.469 | Note 1 | 1.731 | 0.57367 | 231.7737 | 8.5963 | 3.4827 | 5.1136 | 10.901 | 39.8 | 2117 | 56 | 403900.9 | 2.44 | 83.7 | 10.8918 | 10.901 | 8456.58 | 428.01 | 9077.5 | VPC | 4.5072 | 6.6178 | 352.0086 | 4.1968 | 3.9946 | 0.20218 | 0.46949 | 53
Metter | GA0430000 | Candler | 4776 | 141.771 | Note 1 | Note 1 | 143.551 | 117.015 | Note 1 | 2.814 | 1.7944 | 121.6234 | 21.9276 | 3.0969 | 18.8307 | 26.536 | 78.5 | 2267 | 65 | 611524 | 4 | 231.84 | 18.1433 | Note 6 | 12387.62 | 4365.72 | 17821.75 | VPC | 3.7427 | 22.7574 | 657.2111 | 7.3901 | 5.4643 | 1.9258 | 1.0379 | 79.5467
Milledgeville | GA0090001 | Baldwin | 18526 | 1896.62 | Note 1 | 87.656 | 1808.964 | 973.324 | Note 1 | 4.448 | 2.4333 | 980.2053 | 828.7587 | 4.8666 | 823.8921 | 835.64 | 225 | 7652 | 70 | 3510019.73 | 4.6246 | 256.9515 | 60.427 | 835.64 | 22506.18 | 211700.32 | 235974.67 | VPC | 1.7424 | 294.9867 | 10032.1713 | 30.6072 | 2.9412 | 27.666 | 13.6345 | 56
Millen | GA1650000 | Jenkins | 5259 | 192.691 | Note 1 | Note 1 | 198.6505 | 133.472 | Note 1 | 9.625 | 2.4831 | 145.5801 | 53.0704 | 6.7927 | 46.2777 | 65.1785 | 50 | 2025 | 60 | 186161.49 | 2.25 | 402.21 | 12.5761 | Note 6 | 15283.53 | 18613.35 | 38766.89 | VPC | 9.1902 | 62.6115 | 2535.7645 | 16.7392 | 7.5474 | 9.1918 | 3.6798 | 57.7412
Monroe | GA2970001 | Walton | 23376 | 1432.57 | Note 1 | 469.91 | 961.71 | 689.1 | Note 1 | Note 1 | 14.33 | 703.43 | 258.28 | 12.8498 | 245.4302 | 272.61 | 237 | 10779 | 60 | 6576971 | 4.8 | 631.56 | 63.4885 | Note 6 | 61679.09 | 155003.89 | 225733.23 | VPC | 3.2661 | 62.3816 | 2837.1792 | 20.1023 | 5.7222 | 14.3802 | 3.8657 | 78.4919
Montezuma | GA1930003 | Macon | 4547 | 121.735 | Note 1 | Note 1 | 121.735 | 92.6 | 0.288 | Note 1 | 0.23222 | 93.1202 | 28.6148 | 0.46444 | 28.1503 | 28.847 | 38 | 1684 | 55 | Note 5 | 4 | 594.14 | 9.198 | 28.847 | 1857.76 | 16725.24 | 18720.97 | VPC | 0.7556 | 45.7982 | 2029.5847 | 11.035 | 1.1032 | 9.9319 | 3.0605 | 70
Monticello | GA1590000 | Jasper | 3505 | 193.05 | Note 1 | Note 1 | 196.9898 | 150.56 | Note 1 | 33.87 | 0.3764 | 184.8064 | 12.1834 | 0.7528 | 11.4306 | 46.4298 | 29.5 | 2092 | 75 | 785029 | 5.14 | 794.32 | 12.9592 | 46.4298 | 3869.39 | 9079.55 | 40151.54 | VPC | 0.98588 | 14.9697 | 1061.5831 | 6.1897 | 1.8496 | 4.3401 | 0.88205 | 33
Moultrie | GA0710004 / GA0710021 | Colquitt | 12526 | 1131.287 | Note 1 | Note 1 | 1154.3745 | 771.609 | Note 1 | Note 1 | 173.342 | 944.951 | 209.4235 | 27.7222 | 181.7012 | 382.7655 | 212.41 | 8351 | 65 | Note 5 | 2.4 | 229.92 | 56.9824 | 382.7655 | 66533.38 | 41776.75 | 148164.92 | VPC | 9.0949 | 59.611 | 2343.6356 | 12.9697 | 7.9671 | 5.0026 | 3.1887 | 69
Nashville | GA0190002 | Berrien | 4542 | 225.739 | Note 1 | Note 1 | 253.6393 | 182.1 | Note 1 | 1.755 | 3.1705 | 187.0255 | 66.6138 | 10.7659 | 55.8479 | 71.5393 | 85 | 2300 | 60 | 575000 | 2.95 | 274.58 | 17.6262 | Note 6 | 31759.49 | 15334.72 | 48446.65 | VPC | 12.8242 | 66.5252 | 1800.0937 | 20.4757 | 13.8085 | 6.6673 | 3.1685 | 53.3847
Newnan | GA077002 | Coweta | 51115 | 1947.63 | 43.35 | 575.786 | 1415.6363 | 1184.073 | Note 1 | 53.352 | 2.9602 | 1240.3852 | 175.2511 | 5.9204 | 169.3308 | 231.5633 | 267.67 | 20446 | 85 | 12526667 | 7.82 | 543.62 | 140.0777 | 231.5633 | 46297.25 | 92051.58 | 168961.27 | VPC | 0.79332 | 22.69 | 1733.1785 | 6.7665 | 2.2644 | 4.5022 | 1.2088 | 77
Newton County Water & Sewerage Authority | GA2170097 / GA2170004 | Newton | 73777 | Note 1 | 4971.87 | 2924.031 | 2049.7695 | 1921.65 | Note 1 | 3.357 | 4.8041 | 1929.8111 | 119.9584 | 38.9231 | 81.0353 | 128.1195 | 671 | 27740 | 100 | Note 5 | 5 | 2337.69 | 284.3755 | 128.1195 | 194479.28 | 189435.52 | 402992.98 | VPC | 3.8442 | 8.0034 | 330.8713 | 13.8398 | 7.0108 | 6.829 | 0.28496 | 59
North Fulton County | GA1210005 | Fulton | 437032 | Note 1 | 10189.02 | 21.94 | 10159.9417 | 9117.09 | Note 1 | 3.72 | 22.7927 | 9143.6027 | 1016.339 | 205.2089 | 811.1301 | 1042.8517 | 1544.87 | 79572 | 98.1 | 28140769.41 | 4.4 | 536.86 | 726.6409 | 1042.8517 | 902667.68 | 435463.29 | 1352364.59 | VPC | 7.0655 | 27.9278 | 1438.4862 | 16.8166 | 11.344 | 5.4726 | 1.1163 | 65
Notla Water Authority | GA2910003 | Union | 17306 | 347.924 | Note 1 | Note 1 | 358.6845 | 243.919 | Note 1 | 1.483 | 27.795 | 273.197 | 85.4875 | 1.2441 | 84.2434 | 114.7655 | 549.2 | 7224 | 117.3 | 2512094.56 | 0.22 | 567.7 | 173.603 | 114.7655 | 12713.66 | 47824.98 | 77159.75 | VPC | 0.47184 | 31.9496 | 420.2546 | 8.3802 | 1.7599 | 6.6203 | 0.48526 | 84
Oconee County Water Resources Dept. | GA2190000 | Oconee | 21897 | 38.718 | 1145.013 | 50.203 | 1133.528 | 992.808 | Note 1 | 26.453 | 14.1691 | 1033.4301 | 100.0979 | 6.9493 | 93.1486 | 140.72 | 348 | 12120 | 82.3 | 3193002 | 8.76 | 1778.5 | 111.1666 | Note 6 | 60875.61 | 165664.84 | 298786.85 | VPC | 1.5709 | 21.0562 | 733.3383 | 18.6915 | 5.0227 | 13.6687 | 0.83792 | 58.7529
Oglethorpe | GA1930003 | Macon | 6789 | 151.367 | Note 1 | Note 1 | 159.3337 | 109.079 | Note 1 | 0.662 | 0.2727 | 110.0137 | 49.32 | 3.3593 | 45.9607 | 50.2547 | 45.12 | 819 | 47.5 | 624555 | 2.66 | 541.19 | 6.362 | 50.2547 | 8899.68 | 24873.48 | 34279.02 | VPC | 11.2374 | 153.7482 | 2790.7753 | 41.2371 | 10.8665 | 30.3706 | 7.2243 | 69
Palmetto | GA1210008 | Fulton | 5000 | 98.931 | 52.986 | Note 1 | 153.4236 | 95.399 | Note 1 | 0.512 | 0.2385 | 96.1495 | 57.2741 | 3.4433 | 53.8308 | 58.0246 | 34.5 | 1651 | 55 | Note 5 | 7.01 | 3275.12 | 8.7185 | 58.0246 | 24078.49 | 176302.17 | 202838.63 | VPC | 5.714 | 89.3286 | 4274.8264 | 121.3693 | 14.5842 | 106.7851 | 6.1743 | 61
Paulding County Water System | GA2230002 | Paulding | 173780 | 3516.5 | 1761.87 | 349.8 | 4941.8723 | 3327.08 | Note 1 | Note 1 | 8.3177 | 3335.3977 | 1606.4746 | 84.535 | 1521.9396 | 1614.7923 | 1016.5 | 55373 | 100 | Note 5 | 9.8 | 1379.55 | 503.8903 | 1614.7923 | 828442.92 | 2099591.8 | 2939509.4 | VPC | 4.1826 | 75.302 | 4102.0143 | 52.8784 | 14.9611 | 37.9172 | 3.0204 | 68
Pelham | GA2050003 | Mitchell | 6789 | 213.027 | Note 1 | Note 1 | 175.6924 | 104.42 | Note 1 | 0.771 | 0.26105 | 105.452 | 70.2403 | 2.6689 | 67.5715 | 71.2724 | 47 | 1507 | 56 | Note 5 | 2.65 | 425.22 | 9.8177 | 71.2724 | 7037.46 | 28732.74 | 36209.05 | VPC | 4.852 | 122.8449 | 3938.8788 | 23.736 | 4.6698 | 19.0662 | 6.8826 | 62
Perry | GA1530006 | Houston | 22658 | 788.548 | Note 1 | Note 1 | 780.736 | 592.966 | Note 1 | Note 1 | 1.4824 | 594.4484 | 186.2875 | 8.9544 | 177.3332 | 187.77 | 165.1 | 8473 | 63.58 | 2007245 | 3.82 | 357 | 50.2226 | 187.77 | 34205.75 | 63307.94 | 98042.91 | VPC | 2.8954 | 57.3403 | 2942.7272 | 11.5088 | 4.037 | 7.4717 | 3.5309 | 73
Pickens County Water | GA2270002 | Pickens | 7153 | Note 1 | 377.9251 | 118.9315 | 266.7063 | 211.2345 | Note 1 | 0.189 | 0.52809 | 211.9516 | 54.7548 | 5.3709 | 49.3838 | 55.4718 | 145.8 | 3765 | 110 | Note 5 | 5.98 | 3467.4088 | 54.3441 | 55.4718 | 32108.52 | 171233.91 | 205828.85 | VPC | 3.9083 | 35.9358 | 927.9708 | 54.0086 | 8.5282 | 45.4805 | 0.90872 | 62
Polk County Water Authority | GA2330001 | Polk | 25000 | 662.52 | 7.035 | 2.783 | 666.6341 | 601.953 | Note 1 | 12.236 | 8.3329 | 622.5219 | 44.1121 | 15.7059 | 28.4062 | 64.6811 | 500 | 9489 | 97 | 3512121 | 8.12 | 831.85 | 146.1642 | Note 6 | 127532.21 | 230658.31 | 375300.78 | CRUC | 4.5347 | 8.2016 | 155.6504 | 37.748 | 13.44 | 24.308 | 0.19434 | 71.5403
Pooler | GA0510001 | Chatham | 26000 | 390.571 | 697.215 | 3.139 | 1084.647 | 932.772 | Note 1 | 2.089 | 2.3319 | 937.1929 | 147.4541 | 7.0069 | 140.4472 | 151.875 | 117 | 11285 | 56 | 3949839 | 13.53 | 6194.86 | 47.5377 | 151.875 | 94764.55 | 870050.74 | 992202.33 | VPC | 1.7011 | 34.0972 | 3288.7765 | 85.4954 | 8.3974 | 77.098 | 2.9544 | 61
Port Wentworth | GA0510002 | Chatham | 5500 | Note 1 | 475.7967 | Note 1 | 475.7967 | 5.0435 | Note 1 | 54.968 | 5.9475 | 65.959 | 409.8377 | 1.2021 | 408.6356 | 470.7532 | 53.28 | 17050 | 65 | 2015196 | 2.29 | 2286.1 | 67.5153 | Note 6 | 2747.93 | 934115.42 | 1076122.29 | CRUC | 0.19316 | 65.6627 | 21012.5668 | 54.948 | 0.16117 | 54.7868 | 6.0525 | 57.6961
Quitman | GA0270002 | Brooks | 4860 | 453.153 | Note 1 | Note 1 | 458.8891 | 157.92 | Note 1 | Note 1 | 0.3948 | 158.3148 | 300.5743 | 40.2696 | 260.3047 | 300.9691 | 50 | 2741 | 62.3 | 1227720 | 3.18 | 52.29 | 15.5004 | 300.9691 | 128057.33 | 13611.33 | 141689.31 | VPC | 40.2509 | 260.1837 | 14263.272 | 51.685 | 46.7192 | 4.9658 | 16.7934 | 33
Reynold Water System | GA1330046 | Greene | 10000 | 390.8 | Note 1 | Note 1 | 397.7608 | 332.5 | Note 1 | Note 1 | 0.83125 | 333.3313 | 64.4296 | 5.0211 | 59.4085 | 65.2608 | 221.4 | 4126 | 77 | Note 5 | 12.65 | 1513.84 | 51.0576 | 65.2608 | 63516.74 | 89934.93 | 154710.05 | VPC | 3.3341 | 39.4481 | 735.1534 | 37.1914 | 15.3943 | 21.7971 | 1.1636 | 41
Richmond Hill | GA0290000 | Bryan | 15816 | 790.324 | Note 1 | Note 1 | 675.4906 | 526.53 | Note 1 | 1.42 | 8.4436 | 536.3936 | 139.097 | 8.3379 | 130.7591 | 148.9606 | 98.34 | 7151 | 52 | 127274 | 3.4 | 188.55 | 30.4566 | Note 6 | 28348.79 | 24654.63 | 54863.21 | VPC | 3.1944 | 50.0971 | 3642.9131 | 7.412 | 3.9643 | 3.4477 | 4.2933 | 66.4977
Rincon | GA1030001 | Effingham | 11016 | 342.208 | Note 1 | Note 1 | 342.208 | 233.36 | Note 1 | 0.567 | 4.2776 | 238.2046 | 104.0034 | 3.8018 | 100.2016 | 108.848 | 70 | 7395 | 65 | 112000 | 4.5 | 327.28 | 35.3016 | Note 6 | 17108.19 | 32793.97 | 51487.7 | VPC | 1.4085 | 37.123 | 3921.784 | 6.7481 | 2.3135 | 4.4346 | 2.8384 | 65.0882
Ringgold | GA0470002 | Catoosa | 2743 | 145.9 | 36.135 | Note 1 | 182.035 | 143.956 | Note 1 | 5.416 | 0.35989 | 149.7319 | 32.3031 | 0.71978 | 31.5833 | 38.079 | 28 | 1386 | 99.8 | 501685 | 4.12 | 352.395 | 13.0911 | 38.079 | 2965.49 | 11129.81 | 16130.7 | VPC | 1.4228 | 62.4312 | 3090.3454 | 10.1698 | 2.1396 | 8.0302 | 2.4126 | 67
Rockdale County Water Resources | GA2470000 | Rockdale | 92983 | 4215.97 | Note 1 | 8.33 | 4337.7732 | 3247.088 | Note 1 | 37.063 | 24.184 | 3308.335 | 1029.4382 | 49.4087 | 980.0295 | 1090.6852 | 688 | 29446 | 100 | 16267367 | 7.569 | 286.536 | 297.0728 | 1090.6852 | 371247.95 | 280813.74 | 669611.16 | VPC | 4.5971 | 91.1843 | 3902.6343 | 22.1443 | 12.6078 | 9.5366 | 3.299 | 73
Rockmart | GA2330002 | Polk | 4732 | 519.68 | Note 1 | Note 1 | 519.888 | 373.385 | Note 1 | 6.581 | 0.93346 | 380.8995 | 138.9885 | 5.705 | 133.2835 | 146.503 | 67.5 | 3616 | 60 | 1908503.94 | 6.71 | 268 | 19.8759 | 146.503 | 37852.09 | 35719.99 | 75585.95 | VPC | 4.3225 | 100.9846 | 5409.7829 | 20.3463 | 10.4679 | 9.8783 | 6.7058 | 64
Rome | GA1150002 | Floyd | 45586 | 2227 | Note 1 | 172 | 2055 | 1670 | 2.4 | 115 | 50.1 | 1837.5 | 217.5 | 113.175 | 104.325 | 382.6 | 300 | 19130 | 85 | 6517066 | 4.22 | 710 | 139.3798 | Note 6 | 478085.78 | 74070.75 | 669377.53 | VPC | 16.2085 | 14.941 | 952.7397 | 28.8634 | 24.9914 | 3.872 | 0.74849 | 76.6701
Roswell | GA1210009 | Fulton | 18500 | 656.349 | 8.05 | Note 1 | 654.3496 | 503.18 | Note 1 | 12.097 | 2.25 | 517.527 | 136.8226 | 3.0099 | 133.8127 | 151.1696 | 89.9 | 5862 | 88.8 | 5058138 | 9.6 | 418.61 | 44.2637 | 151.1696 | 28788.56 | 56015.35 | 90809.71 | VPC | 1.4067 | 62.5401 | 4077.9783 | 14.4667 | 4.911 | 9.5557 | 3.0231 | 85
Sandersville | GA3030005 | Washington | 5654 | 706.0548 | Note 1 | 78.2094 | 625.9164 | 334.4014 | Note 1 | 12.7643 | 0.836 | 348.0017 | 277.9147 | 1.672 | 276.2427 | 291.515 | 70.3 | 2820 | 55.2941 | 1223384.76 | 5.6051 | 104.9992 | 16.2129 | 291.515 | 9371.71 | 29005.26 | 39804.99 | VPC | 1.6244 | 268.3792 | 10765.7078 | 13.6089 | 3.3233 | 10.2856 | 17.0384 | 67
Satilla Regional Water & Sewer Authority / Satilla Regional Water & Sewer Authority-East | GA2990001 / GA2990051 | Ware | 14311 | 403.837 | Note 1 | Note 1 | 407.9162 | 367.374 | Note 1 | Note 1 | 5.099 | 372.473 | 35.4432 | 3.7843 | 31.6589 | 40.5422 | 236 | 6955 | 52 | 1677373 | 2.8 | 253.11 | 44.0338 | Note 6 | 10596.11 | 8013.18 | 19899.89 | VPC | 1.4907 | 12.4711 | 367.5283 | 2.6757 | 1.5235 | 1.1521 | 0.71897 | 80.9
Savanna-Georgetown Gateway | GA0510081 | Chatham | 17070 | 782.2575 | Note 1 | Note 1 | 782.2575 | 550.1174 | Note 1 | 0.9216 | 1.3753 | 552.4143 | 229.8431 | 13.9963 | 215.8469 | 232.14 | 152 | 6540 | 52.068 | 1836069 | 2.8 | 196.79 | 34.2718 | 232.14 | 52322.16 | 42476.5 | 95250.67 | VPC | 5.8633 | 90.4222 | 3890.5345 | 14.4952 | 8.0003 | 6.4949 | 6.2981 | 49
Savannah-Main | GA0510003 | Chatham | 153355 | 5350.0669 | 1145.652 | 47.5701 | 6452.9682 | 5405.2135 | Note 1 | 152.6625 | 13.513 | 5571.3891 | 881.5791 | 140.4521 | 741.127 | 1047.7547 | 967 | 59144 | 55.5 | 12432650 | 1.82 | 170.24 | 285.6929 | 1047.7547 | 334668.31 | 126169.46 | 489127.5 | VPC | 6.5062 | 34.3312 | 2099.7777 | 7.7918 | 5.6585 | 2.1333 | 2.5941 | 49
Savannah-Quarters | GA0510259 | Chatham | 4327 | 119.9944 | Note 1 | 10.0815 | 109.9129 | 101.1823 | Note 1 | 5.432 | 0.25296 | 106.8672 | 3.0457 | 0.50591 | 2.5398 | 8.7306 | 20.6 | 1803 | 56.87 | 293855 | 3.13 | 296.2 | 7.9272 | 8.7306 | 1583.5 | 752.28 | 4019.67 | VPC | 0.76875 | 3.8593 | 337.7819 | 1.2955 | 0.87826 | 0.41724 | 0.32039 | 61
Savannah-Whitemarsh | GA0510250 | Chatham | 4782 | 233.5113 | Note 1 | Note 1 | 233.5113 | 179.7881 | Note 1 | 0.3471 | 0.44947 | 180.5847 | 52.9266 | 4.5752 | 48.3514 | 53.7232 | 25.33 | 1711 | 59.94 | 513264 | 2.67 | 186.16 | 8.6131 | 53.7232 | 16306.06 | 9001.1 | 25455.44 | VPC | 7.326 | 77.4224 | 5229.753 | 14.7909 | 9.5301 | 5.2607 | 5.6137 | 59
Savannah-Wilmington | GA0510229 | Chatham | 13980 | 492.1693 | Note 1 | Note 1 | 492.1693 | 385.2947 | Note 1 | Note 1 | 0.96324 | 386.2579 | 105.9114 | 9.7896 | 96.1218 | 106.8746 | 58 | 5289 | 53.55 | 1106966 | 2.9 | 163.32 | 21.6397 | 106.8746 | 37951.81 | 15698.61 | 53807.73 | VPC | 5.0711 | 49.7915 | 4540.4705 | 10.1438 | 7.1756 | 2.9682 | 4.4419 | 55
Senoia | GA0770003 | Coweta | 5245 | 120.065 | 69.649 | Note 1 | 190.0615 | 169.873 | Note 1 | 3.102 | 0.42468 | 173.3997 | 16.6619 | 0.84936 | 15.8125 | 20.1885 | 68 | 2601 | 64.6 | Note 5 | 8.58 | 1658.03 | 17.8736 | 20.1885 | 7287.55 | 26217.6 | 39352.49 | VPC | 0.89467 | 16.6559 | 637.087 | 12.8816 | 2.8018 | 10.0798 | 0.88469 | 59
Smyrna | GA0670007 | Cobb | 56980 | Note 1 | 1497.64 | Note 1 | 1426.3238 | 1256.864 | 8.82 | 19.324 | 3.1642 | 1288.1722 | 138.1516 | 6.3284 | 131.8232 | 160.6398 | 185.5 | 15303 | 113.5 | 12684226 | 5.73 | 3373.96 | 136.6695 | 160.6398 | 36261.85 | 444766.13 | 556902.3 | VPC | 1.133 | 23.6006 | 1946.9509 | 31.4336 | 2.3696 | 29.064 | 0.96454 | 67
Social Circle | GA2970002 | Walton | 4800 | 81.62 | 131.61 | Note 1 | 213.8826 | 149.24 | Note 1 | 6.64 | 0.3731 | 156.2531 | 57.6295 | 2.3207 | 55.3087 | 64.6426 | 24.5 | 2502 | 60 | Note 5 | 19.79 | 2158.1837 | 11.1218 | 64.6426 | 44744.99 | 119366.43 | 179246.97 | VPC | 2.5413 | 60.5639 | 6184.9305 | 65.5921 | 17.8837 | 47.7084 | 4.973 | 66
South Atlantic Utilities-Bryan County | GA0290080 | Bryan | 3599 | 168.679 | Note 1 | Note 1 | 168.679 | 131.367 | Note 1 | Note 1 | 0.32842 | 131.6954 | 36.9836 | 0.65683 | 36.3267 | 37.312 | 12 | 1333 | 45 | Note 5 | 3.12 | 215.69 | 4.3505 | 37.312 | 2049.33 | 7835.32 | 9955.48 | VPC | 1.35 | 74.6627 | 8293.778 | 7.4153 | 1.5374 | 5.878 | 8.35 | 46
South Monroe County Water System | GA2070074 | Monroe | 11817 | Note 1 | 336.71 | 17.318 | 319.392 | 275.562 | Note 1 | 1.886 | 1.294 | 278.742 | 40.65 | 1.3778 | 39.2722 | 43.83 | 142.5 | 5397 | 64 | Note 5 | 8.64 | 2827 | 36.9199 | 43.83 | 11904.28 | 111022.48 | 131916.62 | VPC | 0.69943 | 19.9361 | 755.0529 | 22.7769 | 2.2057 | 20.5711 | 1.0637 | 52
Spalding County Water System | GA2550036 | Spalding | 40430 | Note 1 | 1091.8 | Note 1 | 1091.8 | 819.6311 | Note 1 | 11.2753 | 28.2311 | 859.1376 | 232.6624 | 13.0868 | 219.5756 | 272.1689 | 535 | 15379 | 99 | 7403223.35 | 11.64 | Note2/B | 187.9454 | Note 6 | 152330.39 | Note 4 | 152330.39 | CRUC | 2.3314 | 39.1168 | 1124.4431 | 9.9051 | 9.9051 | 0 | 1.1683 | 53.9706
Sparta | GA1410001 | Hancock | 3354 | 277.85 | Note 1 | 38.3548 | 241.9337 | 173.6515 | Note 1 | 4.457 | 0.43413 | 178.5427 | 63.391 | 3.5806 | 59.8105 | 68.2822 | 53 | 1717 | 59 | Note 5 | 11.2 | 809.19 | 11.7211 | 68.2822 | 39397.13 | 48398.03 | 91753.02 | VPC | 5.7133 | 95.4364 | 3091.7791 | 51.1329 | 22.9453 | 28.1876 | 5.1028 | 49
St. Marys | GA0390001 | Camden | 7265 | 570.817 | Note 1 | Note 1 | 570.817 | 500.7444 | Note 1 | Note 1 | 1.2519 | 501.9963 | 68.8207 | 2.5037 | 66.317 | 70.0726 | 131 | 8220 | 55.5 | Note 5 | 3.07 | 336.04 | 39.3342 | 70.0726 | 7686.43 | 22285.16 | 30392.26 | VPC | 0.83449 | 22.1034 | 1386.9491 | 3.6462 | 0.93509 | 2.7111 | 1.686 | 51
Statesboro | GA0310004 | Bulloch | 36846 | 1373.466 | Note 1 | Note 1 | 1363.069 | 1219.543 | Note 1 | Note 1 | 17.0384 | 1236.5814 | 126.4876 | 18.7751 | 107.7125 | 143.526 | 251.2 | 14730 | 62.3 | 2178598.95 | 4.07 | 245.13 | 81.1457 | Note 6 | 76414.84 | 26403.56 | 106995.01 | VPC | 3.4921 | 20.0341 | 1174.772 | 6.9802 | 5.1877 | 1.7925 | 1.3274 | 65.5685
Statham | GA0130001 | Barrow | 3986 | 39.418 | 82.569 | Note 1 | 121.987 | 98.376 | Note 1 | 0.6157 | 1 | 99.9916 | 21.9954 | 3.5535 | 18.4419 | 23.611 | 52 | 2009 | 83 | Note 5 | 13.6328 | 2828.008 | 17.652 | 23.611 | 48238.13 | 52153.77 | 104961.1 | VPC | 4.846 | 25.1497 | 971.6478 | 49.9711 | 24.011 | 25.9601 | 1.0447 | 60
Stockbridge | GA1510004 | Henry | 7195 | 92.4 | 191.4497 | Note 1 | 292.2102 | 215.727 | Note 1 | 7.188 | 15.6 | 238.515 | 53.6952 | 5.6279 | 48.0673 | 76.4832 | 49 | 2754 | 93 | 2238828.22 | 8.21 | 2836.27 | 23.0212 | 76.4832 | 45416.94 | 136331.86 | 246381.71 | VPC | 5.5988 | 47.8182 | 2687.5765 | 65.9945 | 16.4913 | 49.5032 | 2.088 | 62
Summerville | GA0550003 | Chattooga | 11651 | 868.337 | Note 1 | Note 1 | 838.9729 | 526.845 | Note 1 | Note 1 | 10.4872 | 537.3322 | 301.6408 | 22.5229 | 279.1179 | 312.1279 | 225 | 5198 | 80 | 2115000 | 6.05 | 397.63 | 58.3109 | Note 6 | 136263.62 | 110985.64 | 251419.27 | VPC | 11.8712 | 147.1155 | 3398.6956 | 47.5662 | 26.2146 | 21.3516 | 4.7867 | 62.7444
Swainsboro | GA1070031 | Emanuel | 7438 | 414.414 | Note 1 | Note 1 | 414.414 | 276.9651 | Note 1 | 2.3487 | 0.69241 | 280.0063 | 134.4078 | 4.2062 | 130.2016 | 137.4489 | 97.15 | 3602 | 52 | Note 5 | 7.22 | 252.505 | 20.2304 | 137.4489 | 30203.3 | 32876.56 | 63847.76 | VPC | 3.1993 | 99.033 | 3671.8141 | 17.5125 | 8.3851 | 9.1273 | 6.4359 | 64
Sylvania | GA2510003 | Screven | 4910 | 241.134 | Note 1 | Note 1 | 244.0628 | 148.964 | Note 1 | 0.283 | 3.0508 | 152.2978 | 91.765 | 8.8377 | 82.9273 | 95.0988 | 127 | 1655 | 60 | 1547500 | 4.44 | 371.57 | 20.4835 | Note 6 | 39239.26 | 30813.3 | 71291.29 | VPC | 14.6301 | 137.2798 | 1788.9612 | 42.3278 | 23.7095 | 18.6183 | 4.0485 | 36.9441
Sylvester | GA3210003 | Worth | 5865 | 332.676 | Note 1 | Note 1 | 339.4653 | 206.722 | Note 1 | Note 1 | 4.2433 | 210.9653 | 128.5 | 4.5135 | 123.9865 | 132.7433 | 82.1 | 3087 | 80 | 1467450.49 | 5.96 | 430.32 | 26.4906 | Note 6 | 26905.09 | 53353.86 | 82084.93 | VPC | 4.0058 | 110.0385 | 4137.5026 | 25.999 | 8.7156 | 17.2834 | 4.6804 | 73.2516
Talbot County Water Works | GA2630005 | Talbot | 3879 | Note 1 | 196.9756 | 54.8364 | 142.1392 | 130.9805 | Note 1 | 1.6544 | 0.32745 | 132.9624 | 9.1768 | 3.3617 | 5.815 | 11.1587 | 150 | 1579 | 80 | Note 5 | 7.26 | 3053.7171 | 30.6118 | 11.1587 | 24264.19 | 17757.52 | 48073.87 | VPC | 5.833 | 10.0897 | 106.2109 | 26.6129 | 15.3668 | 11.2461 | 0.18996 | 37
Tallapoosa | GA1430002 | Haralson | 3256 | Note 1 | 190.775 | Note 1 | 194.6684 | 140.718 | Note 1 | Note 1 | 0.35179 | 141.0698 | 53.5986 | 0.73174 | 52.8668 | 53.9504 | 31 | 1773 | 80 | Note 5 | 7.55 | 2920 | 12.6629 | 53.9504 | 5524.63 | 154371.15 | 160923.03 | VPC | 1.1307 | 81.6924 | 4672.2787 | 90.1837 | 3.116 | 87.0678 | 4.1749 | 67
Temple | GA0450005 | Carroll | 2560 | Note 1 | 163.8337 | Note 1 | 163.8337 | 134.613 | Note 1 | 0.31871 | 0.33653 | 135.2682 | 28.5655 | 2.036 | 26.5294 | 29.2207 | 44 | 2560 | 50 | 1409511.55 | 5.29 | 3688.74 | 11.3522 | 29.2207 | 10765.35 | 97860.21 | 111042.56 | VPC | 2.179 | 28.392 | 1651.8955 | 42.4319 | 4.2052 | 38.2266 | 2.3369 | 62
The Landings Subdivision | GA0510033 | Chatham | 12100 | 513.307 | Note 1 | Note 1 | 509.825 | 466.598 | Note 1 | 0.105 | 0.2 | 466.903 | 42.922 | 6.2307 | 36.6913 | 43.227 | 95.4 | 4722 | 56.4 | 797373 | 4.8 | 498.5 | 25.2058 | 43.227 | 29902.64 | 176118.4 | 207485.04 | CRUC | 3.6151 | 21.2885 | 1053.7128 | 43.63 | 6.3326 | 37.2974 | 1.4557 | 82
Thomaston | GA2930000 | Upson | 9816 | 625.9 | Note 1 | 48.013 | 577.887 | 398.416 | Note 1 | 5.122 | 0.99604 | 404.534 | 173.353 | 14.4726 | 158.8803 | 179.471 | 114 | 4928 | 84.07 | 4510084.87 | 7.19 | 632.51 | 41.6078 | 179.471 | 103019.47 | 100493.39 | 207382.59 | VPC | 8.0461 | 88.3297 | 3818.3207 | 41.2973 | 20.9049 | 20.3923 | 3.8185 | 69
Thomasville | GA2750005 | Thomas | 24206 | 2054.029 | Note 1 | Note 1 | 2028.6706 | 1530.195 | Note 1 | 16.8 | 25.3584 | 1572.3534 | 456.3172 | 48.5637 | 407.7535 | 498.4756 | 275.3 | 14289 | 66.3 | 5521000 | 5.26 | 560 | 87.9101 | Note 6 | 255445.08 | 228341.98 | 507395.75 | VPC | 9.3114 | 78.1813 | 4057.8749 | 33.8573 | 17.877 | 15.9803 | 4.6383 | 75.9216
Thomson-McDuffie Co. W&S Comm | GA1890001 | McDuffie | 17717 | 700.27 | Note 1 | Note 1 | 700.27 | 517.23 | Note 1 | Note 1 | 28.5 | 545.73 | 154.54 | 13.1419 | 141.3981 | 183.04 | 280 | 7455 | 62 | 3755259 | 9.81 | 628.08 | 59.5859 | 183.04 | 128921.69 | 88809.34 | 235631.31 | VPC | 4.8297 | 51.9641 | 1383.5434 | 29.206 | 17.2933 | 11.9127 | 2.373 | 76
Tifton-Tift County Water System | GA2770001 | Tift | 30940 | 1820.92 | Note 1 | Note 1 | 1820.92 | 1404.881 | Note 1 | Note 1 | 3.5122 | 1408.3932 | 412.5268 | 40.0973 | 372.4295 | 416.039 | 286.5 | 12401 | 58.7 | 3907037 | 1.43 | 320.06 | 73.0634 | 416.039 | 57339.2 | 119199.77 | 177663.09 | VPC | 8.8586 | 82.28 | 3561.4473 | 14.2359 | 4.6238 | 9.6121 | 5.0973 | 66
Toccoa | GA2570001 | Stephens | 24960 | 1704.61 | Note 1 | 455.614 | 1248.996 | 681.81 | Note 1 | 176.598 | 0.545 | 858.953 | 390.043 | 28.1369 | 361.9061 | 567.186 | 613.7 | 11333 | 125 | 5858734 | 7.27 | 424.63 | 229.0406 | 567.186 | 169731.25 | 153676.21 | 398627.69 | VPC | 6.802 | 87.49 | 1615.6488 | 28.5368 | 14.9767 | 13.5601 | 1.5801 | 63
Towns County Water & Sewerage Authority | GA2810007 | Towns | 11229 | Note 1 | 266.612 | Note 1 | 266.612 | 157.007 | Note 1 | 0.022 | 4.528 | 161.557 | 105.055 | 1.053 | 104.002 | 109.605 | 204 | 4626 | 100 | 2205914 | 5.9 | 2692.84 | 65.6102 | 109.605 | 6212.79 | 280060.65 | 298525.86 | VPC | 0.62365 | 61.5947 | 1396.7495 | 61.8836 | 1.343 | 60.5406 | 1.5851 | 71
Tybee Island | GA0510005 | Chatham | 27359 | 291.64 | Note 1 | Note 1 | 291.64 | 268.892 | Note 1 | 0.95 | 0.67223 | 270.5142 | 21.1258 | 2.7004 | 18.4253 | 22.748 | 33.9 | 3358 | 62 | Note 5 | 4.42 | 887.46 | 15.5491 | 22.748 | 11919.12 | 16351.73 | 29710.52 | VPC | 2.2032 | 15.0329 | 1489.0952 | 8.419 | 3.5495 | 4.8695 | 1.185 | 51
Union City | GA1210010 | Fulton | 27359 | Note 1 | 566.053 | Note 1 | 582.5388 | 467.017 | Note 1 | 0.964 | 1.1675 | 469.1485 | 113.3903 | 12.8467 | 100.5436 | 115.5218 | 112 | 5277 | 82 | 6055263.39 | 9.9 | 6165.72 | 41.8263 | 115.5218 | 127109.21 | 619923.51 | 760175.22 | VPC | 6.6698 | 52.2005 | 2459.4807 | 141.5639 | 24.0874 | 117.4765 | 2.4038 | 80
Upson County Water Department | GA2930010 | Upson | 5049 | 148.372 | 23.8 | Note 1 | 172.2001 | 153.5 | Note 1 | 0.15 | 0.38375 | 154.0337 | 18.1664 | 5.5196 | 12.6468 | 18.7001 | 71.6 | 2053 | 82 | 905447.36 | 0.41 | 1264.737 | 20.8105 | 18.7001 | 57416.21 | 15994.88 | 74086.15 | VPC | 7.3658 | 16.8771 | 483.9215 | 35.758 | 27.967 | 7.791 | 0.60771 | 69
USAF-Moody Air Force Base Main | GA1850125 | Lowndes | 6109 | 128.698 | Note 1 | Note 1 | 128.698 | 8.837 Note A | Note 1 | 4.224 | 1.6087 | 14.6697 | 114.0283 | 0.47577 | 113.5525 | 119.861 | 50.8 | 518 | 65 | 162800 | 2.97 | 331.26 | Note 3 | Note 6 | 1413.03 | 37615.4 | 40960.58 | VPC | 2.5164 | 600.5845 | 6124.0701 | 75.3445 | 2.7279 | 72.6166 | Note 3 | 59.6765
Note A
USA-Fort Stewart Main | GA1790024 | Liberty | 27573 | 676.45 | Note 1 | Note 1 | 676.45 | 3.6 | 352.5 | Note 1 | 300 | 656.1 | 20.35 | 1.7895 | 18.5605 | 320.35 | 161.7 | 2677 | 57 | 337631 | Note C | 449.12 | 28.9278 | 320.35 | 0 | 8335.88 | 143071.88 | VPC | 1.8315 | 18.9954 | 314.4751 | 3.1139 | 0 | 3.1139 | 0.64161 | 60
USAF-Robins Air Force Base Main | GA1530042 | Houston | 23967 | 582.786 | Note 1 | Note 1 | 582.786 | 122.31 | 314.09 | 4.43 | 7.2848 | 448.1148 | 134.6712 | 5.0125 | 129.6587 | 146.386 | 92 | 1668 | 65 | 740292 | 0.99 | 1270.26 | 23.3656 | Note 6 | 4962.36 | 164700.25 | 184543.48 | VPC | 8.2331 | 212.9672 | 3861.188 | 101.7162 | 2.975 | 98.7412 | 5.5491 | 29.3509
USA-Hunter Army Airfield Main | GA 0510107 | Chatham | 7500 | 154.24 | 0.7 | Note 1 | 154.94 | 18.9 | 57 | Note 1 | 74 | 149.9 | 5.04 | 0.3795 | 4.6605 | 79.04 | 66.4 | 980 | 55 | 149195 | Note C | 967 | 10.1624 | 79.04 | 0 | 4506.7 | 76064.7 | VPC | 1.0609 | 13.0291 | 192.2966 | 4.5987 | 0 | 4.5987 | 0.4586 | 60
USMC-Logistics Base Albany | GA0950035 | Dougherty | 3350 | 89.184 | Note 1 | Note 1 | 89.184 | 19.342 | 18.192 | Note 1 | 0.093835 | 37.6278 | 51.5562 | 0.38304 | 51.1731 | 51.65 | 40.3 | 322 | 65.8 | 228930 | 0.32 | 495.04 | 6.3963 | 51.65 | 122.57 | 25332.74 | 25501.77 | VPC | 3.2591 | 435.4048 | 3478.9164 | 79.0538 | 0.38066 | 78.6731 | 8.0005 | 34
USN-Kings Bay Submarine Base | GA0390013 | Camden | 9730 | 453.5 | Note 1 | Note 1 | 453.5 | 192.987 | 111.215 | Note 1 | 0.7605 | 304.9625 | 148.5375 | 22.964 | 125.5735 | 149.298 | 100 | 500 | 101 | Note 5 | 1.79 | 210.18 | 22.7088 | 149.298 | 41105.58 | 26393.04 | 67658.46 | VPC | 125.8302 | 688.0739 | 3440.3695 | 134.9972 | 82.2112 | 52.7861 | 5.5297 | 70
Utilities, Inc. (Big Canoe Subdivision) | GA2270004 | Pickens | 7522 | 204.344 | Note 1 | Note 1 | 204.578 | 107.338 | Note 1 | 2.424 | 0.26835 | 110.0303 | 94.5477 | 2.7767 | 91.7709 | 97.24 | 94.2 | 3507 | 155 | 1069295 | 6.18 | 2010.61 | 58.5931 | 97.24 | 16953.94 | 567144.31 | 600736.94 | CRUC | 2.1692 | 71.693 | 2669.0784 | 166.5521 | 4.8343 | 161.7178 | 1.5662 | 73
Valdosta | GA1850002 | Lowndes | 64203 | 2832.258 | Note 1 | Note 1 | 2832.258 | 2511.269 | Note 1 | 35.881 | 35.4032 | 2582.5532 | 249.7048 | 19.7427 | 229.9621 | 320.989 | 445 | 23779 | 63 | 4851054 | 2.47 | 310.7 | 137.379 | Note 6 | 48825.36 | 71449.23 | 142422.6 | VPC | 2.2747 | 26.4954 | 1415.805 | 5.058 | 2.0533 | 3.0047 | 1.6739 | 77.8922
Vidalia | GA2790002 | Toombs | 19102 | 626.469 | Note 1 | Note 1 | 626.7824 | 470.882 | Note 1 | 23.114 | 7.8348 | 501.8308 | 124.9516 | 12.8257 | 112.1259 | 155.9004 | 141 | 7075 | 47 | 1462000 | 1.75 | 226.7 | 31.2917 | Note 6 | 22445 | 25418.94 | 54880.03 | VPC | 4.9666 | 43.4197 | 2178.6826 | 6.7652 | 3.1724 | 3.5928 | 3.5832 | 74.1891
Vienna | GA0930004 | Dooly | 4100 | 829.8089 | Note 1 | Note 1 | 828.4006 | 620.1565 | 2 | Note 1 | 1.5554 | 623.7119 | 204.6887 | 15.767 | 188.9216 | 206.2441 | 76 | 1455 | 56 | Note 5 | 4.424 | 182.407 | 12.8651 | 206.2441 | 69753.77 | 34460.63 | 104498.12 | VPC | 29.6889 | 355.7344 | 6810.4408 | 71.625 | 47.9407 | 23.6843 | 14.6848 | 58
Villa Rica | GA0450006 | Carroll | 17000 | 420.094 | 263.747 | Note 1 | 683.5725 | 528.851 | Note 1 | 1.298 | 1.3221 | 531.4711 | 152.1014 | 10.7176 | 141.3838 | 154.7215 | 137.78 | 7098 | 80 | Note 5 | 7.17 | 1409.21 | 52.8546 | 154.7215 | 76731.25 | 199239.45 | 279663.01 | VPC | 4.1368 | 54.5721 | 2811.3866 | 38.8801 | 10.8103 | 28.0698 | 2.675 | 65
Walker County Water & Sewerage Authority | GA2950003 | Walker | 34349 | 1247.053 | Note 1 | 393.95 | 861.7202 | 587.792 | Note 1 | 3.611 | 1.4695 | 592.8725 | 268.8477 | 15.0084 | 253.8393 | 273.9282 | 429.4 | 13211 | 75 | 5847448.49 | 5.47 | 507 | 117.8413 | 273.9282 | 81730.25 | 128696.53 | 213002.59 | VPC | 3.1125 | 52.6418 | 1619.5859 | 15.9281 | 6.1865 | 9.7416 | 2.1541 | 61
Walthourville | GA1790020 | Liberty | 3858 | 132.1675 | Note 1 | Note 1 | 132.1675 | 75.487 | Note 1 | Note 1 | 0.18872 | 75.6757 | 56.4918 | 1.1399 | 55.3519 | 56.6805 | 37 | 1885 | 145.3 | Note 5 | 6.56 | 364.1 | 25.6114 | 56.6805 | 7477.94 | 20153.61 | 27700.26 | VPC | 1.6568 | 80.4504 | 4098.6192 | 14.6586 | 3.9671 | 10.6916 | 2.1612 | 52
Walton County Water Department | GA2970008 | Walton | 44460 | Note 1 | 1796 | 164 | 1648.4848 | 1171 | Note 1 | Note 1 | 2.9275 | 1173.9275 | 474.5573 | 11.7394 | 462.8179 | 477.4848 | 590 | 32712 | 94 | 11000000 | 7.12 | 1350 | 293.8089 | 477.4848 | 83584.69 | 624804.2 | 712341.01 | VPC | 0.98321 | 38.7624 | 2149.1429 | 21.6553 | 2.5552 | 19.1002 | 1.5752 | 77
Warner Robins | GA1530007 | Houston | 80308 | 3179.18 | 865.02 | Note 1 | 4044.2 | 2490.79 | Note 1 | Note 1 | 3.536 | 2494.326 | 1549.874 | 89.4887 | 1460.3853 | 1553.41 | 489.2 | 28459 | 62 | 9262237 | 2.39 | 512.18 | 156.496 | 1553.41 | 213877.97 | 747980.15 | 963669.19 | VPC | 8.615 | 140.5902 | 8178.7728 | 33.798 | 7.5153 | 26.2827 | 9.3318 | 72
Washington | GA3170002 | Wilkes | 6490 | 372.2 | Note 1 | Note 1 | 371.4056 | 175.7618 | Note 1 | Note 1 | 0.4394 | 176.2012 | 195.2044 | 6.3147 | 188.8896 | 195.6438 | 129.2 | 2691 | 80 | Note 5 | 8.8381 | 1802.3559 | 32.1966 | 195.6438 | 55810.53 | 340446.36 | 397048.85 | VPC | 6.4291 | 192.3099 | 4005.4634 | 147.2527 | 20.7397 | 126.513 | 5.8668 | 59
Waycross Water System | GA2990002 | Ware | 14340 | 830.67 | Note 1 | 0.743 | 829.927 | 672 | Note 1 | 7.7 | 1.68 | 681.38 | 148.547 | 24.3816 | 124.1654 | 157.927 | 140 | 6286 | 48 | 1457104 | 1.12 | 166.09 | 29.7893 | 157.927 | 36187.75 | 20622.62 | 58368.29 | VPC | 10.6266 | 54.1169 | 2429.8503 | 9.0376 | 5.7569 | 3.2807 | 4.1681 | 72
Waynesboro | GA0330004 | Burke | 5600 | 307.437 | Note 1 | Note 1 | 307.437 | 193.82 | Note 1 | 34.4 | 0.48455 | 228.7046 | 78.7325 | 0.9691 | 77.7634 | 113.617 | 90.8 | 2435 | 45 | Note 5 | 5.62 | 718.21 | 14.0677 | 113.617 | 5446.34 | 55850.42 | 86351.19 | VPC | 1.0904 | 87.495 | 2346.3687 | 25.1732 | 2.2367 | 22.9365 | 5.5278 | 53
West Point | GA2850002 | Troup | 4140 | 528.062 | 18.81 | 0.897 | 516.0847 | 386 | Note 1 | Note 1 | 54 | 440 | 76.0847 | 9.8076 | 66.2771 | 130.0847 | 86.83 | 1856 | 71 | 2621759.77 | 3.35 | 763.17 | 19.3883 | 130.0847 | 43921.14 | 50580.73 | 135713.05 | VPC | 14.4774 | 97.8347 | 2091.2268 | 50.917 | 23.6644 | 27.2525 | 3.4184 | 64
White County Water & Sewerage Authority | GA3110072 | White | 5918 | 342.45 | 16.048 | 160.689 | 205.07 | 153.631 | Note 1 | Note 1 | 0.748 | 154.379 | 50.691 | 3.1077 | 47.5833 | 51.439 | 166.8 | 2749 | 115 | Note 5 | 0.54 | 1284.96 | 55.1861 | 51.439 | 32755.3 | 61142.62 | 94859.07 | VPC | 3.0972 | 47.4228 | 781.5658 | 34.1571 | 11.9154 | 22.2418 | 0.86223 | 77
Winder | GA0130002 | Barrow | 48000 | 1622.18 | 97.105 | 48.408 | 1670.877 | 1409.398 | Note 1 | 11.269 | 9.004 | 1429.671 | 241.206 | 20.157 | 221.049 | 261.479 | 422 | 18163 | 82 | Note 5 | 6.36 | 380.73 | 149.8736 | 261.479 | 127576.67 | 84159.99 | 219455.2 | VPC | 3.0405 | 33.3433 | 1435.1036 | 11.6576 | 7.024 | 4.6336 | 1.4749 | 57
Woodstock | GA0570003 | Cherokee | 30000 | 129.045 | 667.722 | Note 1 | 796.767 | 582.305 | Note 1 | 45.548 | 1.4558 | 629.3088 | 167.4582 | 4.4851 | 162.9731 | 214.462 | 105.7 | 8278 | 141.7 | 3660396.74 | 7.5 | 2914.01 | 93.797 | 214.462 | 33114.67 | 474905.38 | 644989.48 | VPC | 1.4844 | 53.9384 | 4224.2362 | 61.3699 | 4.0003 | 57.3696 | 1.7375 | 74
Wrightsville | GA1670002 | Johnson | 3846 | 167.001 | Note 1 | Note 1 | 159.0486 | 115.4083 | Note 1 | Note 1 | 1.9881 | 117.3964 | 41.6522 | 12.1001 | 29.552 | 43.6403 | 40.1 | 891 | 60 | 945025 | 1.87 | 0.79 | Note 3 | Note 6 | 22627.28 | 23.48 | 22652.33 | VPC | 37.2066 | 90.8692 | 2019.0628 | 25.4217 | 25.3954 | 0.026352 | Note 3 | 58.1444
| Note 1 | “Note 1” represents N/A. The utility does not have uses that fit into this category.
| Note 2 | “Note 2” indicates the utility does not know what the value for this parameter is.
| Note 3 | “Note 3” indicates that the intended value cannot be calculated. The software does not display a value of UARL or ILI for very small water systems with low connection density or low pressure water distribution system. In summary, the UARL or ILI calculation has not yet been proven as fully valid for very small or low pressure water distribution systems.
| Note 4 | “Note 4” indicates that the intended value cannot be calculated. The software does not display a value for “Annual Cost of Real Losses” because the utility does not know what the value for the “variable production cost” is.
| Note 5 | “Note 5” indicates this input has been made optional in the new V6 software, as it is no longer used in calculating a Performance Indicator.
| Note 6 | "Note 6" indicates this was a submitted V5 audit and this performance indicator was not an input/calculator option in the V5 audit software.
| Note A | Moody Air force Base only consumes its water and does no billing. They also randomly meter certain buildings. Most of the older buildings have no meter in place
| Note B | The variable production cost is not applicable to this utility. Water supply is entirely purchased as bulk water imported at a defined rate. No restriction applies for volume and there are no provisions on any rate adjustment for variable production cost. The City of Griffin does the entire meter reading for Spalding County. This cost is built in through a complex rate structure based on the contract between the County and City. In summary, Spalding County does not know the value for this field.
| Note C | USA-Fort Stewart Main and USA-Hunter Army Airfield Main did not provide a customer retail cost.
Yellow represents negative values (anomalies). Both the utilities and EPD are aware of these negative values (i.e. negative real losses and negative ILI values). These negative values are not credible. They are mostly due to extreme meter inaccuracies. For example, (a) over-estimation of authorized consumption, and/or (b) under-estimation of water supply, and/or (c) over-estimation of apparent losses. To resolve this issue, the utilities with negative values must (a) replace their old meters with new ones, and/or (b) perform high frequency (short intervals) recalibration and accuracy testing on a regular basis.