## Sheet1
Posting Date | 2025-04-16
FACILITY_NAME | BEGIN_DATE | COUNTY | CITY | OVERFLOW_LOCATION | QUANTITY_GALLONS | OVERFLOW_TYPE | PERMIT_NUMBER | SPILL_SOURCE | CAUSE | RIVER_BASIN | WATERWAY_IMPACTED
Cobb County Water System (R.L. Sutton WRF) | 2025-04-14 | Cobb |  | Non-Outfall |  |  | GA0026140
Cobb County Water System (R.L. Sutton WRF) | 2025-04-13 | Cobb |  | Non-Outfall |  |  | GA0026140
Dallas, City of (Pumpkinvine Creek WPCP) | 2025-04-13 | Paulding | Dallas | Near 382 Saddle Brooke Dr. Dallas, GA 30132 | 3600 | Raw Sewage | GA0039241 | WWTP | Grease and rag build up in main sewer line | Coosa | Lawrence Creek
Atlanta, City of (R.M. Clayton, Utoy Creek & South River WRCS) | 2025-04-13 | Fulton | Atlanta | 1064 Ira St SW | 615 |  | GA0039012 | Collection System | debris in the mainline | Upper Ocmulgee | South River
Dekalb County Department of Watershed Management (Snapfinger Creek AWWTF) | 2025-04-12 | DeKalb |  | Non-Outfall | 10 | Raw Sewage | GA0024147 | Collection System
Dekalb County Department of Watershed Management (Snapfinger Creek AWWTF) | 2025-04-11 | DeKalb |  | Non-Outfall |  | Raw Sewage | GA0024147 | Collection System
Macon Water Authority (Rocky Creek WRF) | 2025-04-11 | Bibb |  | Non-Outfall |  | Raw Sewage | GA0024546 | Collection System | High Levels of InflowHigh Levels of Inflow | Ocmulgee | Rocky Creek
City of Fairburn | 2025-04-11 | Fulton | Fairburn | 524 Willoe Creek | 19250 | Raw Sewage | GAU060251 | Collection System | Grease Blockage | Chattahoochee | wetland
Settendown Public Utility, LLC (Hampton Creek WRF) | 2025-04-10 | Forsyth |  | Glenhaven Drive | 8000 | Raw Sewage | GA0038903 | WWTP | Clogged gravity line | Coosa | Settendown Creek
Columbus Water Works (South WRF) | 2025-04-09 | Muscogee |  | Non-Outfall |  | Raw Sewage | GA0020516 | Collection System | Aging InfrastructureAging Infrastructure | Chattahoochee | Mill Branch Creek
Atlanta, City of (R.M. Clayton, Utoy Creek & South River WRCS) | 2025-04-09 | Fulton | Atlanta | 1812 Peachtree St NW | 298 | Raw Sewage | GA0039012 | Collection System | debris in the mainline | Chattahoochee | Peachtree Creek
Milledgeville, City of (Milledgeville WPCP) | 2025-04-09 | Baldwin | Milledgeville | Intersection of Dunlap Rd and N. Jefferson St | 600 | Raw Sewage | GA0030775 | Collection System | Roots | Oconee | Tobler Creek
Columbus Water Works (South WRF) | 2025-04-09 | Muscogee |  | Non-Outfall | 360 | Raw Sewage | GA0020516 | Collection System | Aging InfrastructureAging Infrastructure | Chattahoochee | Upatoi Creek tributary
Atlanta, City of (R.M. Clayton, Utoy Creek & South River WRCS) | 2025-04-09 | Fulton | Atlanta | 2631 Cascade Rd SW | 212 | Raw Sewage | GA0039012 | Pump Station | pump station malfunction and grease in the mainline | Chattahoochee | Utoy Creek
Macon Water Authority (Rocky Creek WRF) | 2025-04-08 | Bibb |  | Non-Outfall |  | Raw Sewage | GA0024546 | Collection System | Blockage Fats Oil GreaseBlockage Fats Oil Grease | Ocmulgee | Wolf Creek
Barnesville, City of (James A. King WWTF) | 2025-04-07 | Lamar | Barnesville | Richardson Lift Station | 34500 | Raw Sewage | GA0021041 | Lift Station | heavy rainfall | Ocmulgee | Big Towaliga Creek Tributary
LaGrange, City of (Long Cane Creek WPCP) | 2025-04-07 | Troup | LaGrange | 311 Creekside Dr. | 98125 | Raw Sewage | GA0036951 | Collection System | Heavy rains created excessive flow, overwhelming nearby lift station. Overflow occurred from lowest manhole on st. | Chattahoochee | Dixie Creek
Barnesville, City of (James A. King WWTF) | 2025-04-07 | Lamar | Barnesville | Aldora Lift Station | 156400 | Raw Sewage | GA0021041 | Lift Station | heavy rainfall and i pump out for repair | Ocmulgee | Little Potato Creek Tributary
Dekalb County Department of Watershed Management (Snapfinger Creek AWWTF) | 2025-04-07 | DeKalb |  | Non-Outfall |  | Raw Sewage | GA0024147 | Collection System |  |  | Panthers Branch
Macon Water Authority (Rocky Creek WRF) | 2025-04-07 | Bibb |  | Non-Outfall |  | Raw Sewage | GA0024546 | Collection System |  | Ocmulgee | Rocky Creek
Cobb County Water System (R.L. Sutton WRF) | 2025-04-07 | Cobb |  | Non-Outfall | 380 | Raw Sewage | GA0026140 | Collection System | Blockage Rags wipesBlockage Rags wipes | Chattahoochee | Sope Creek
Thomaston, City of (Town Branch WPCP) | 2025-04-07 |  | Thomaston | Highway 74 Lift Station | 4800 | Raw Sewage | GA0030121 | Lift Station | Pump blockage | Flint | Town Branch
Adairsville, City of (North WPCP) | 2025-04-07 | Bartow |  | Non-Outfall |  |  | GA0046035 |  | Hurricane or Large Stormwater EventHurricane or Large Stormwater Event |  | Tributary of Oothacalooga Creek
Eastman, City of (Sugar Creek WPCP) | 2025-04-07 | Dodge |  | Non-Outfall | 8000 | Raw Sewage | GA0046485 | Pump Station | Hurricane or Large Stormwater EventHurricane or Large Stormwater Event | Ocmulgee | Tributary to Sugar Creek
Gwinnett County Board of Commissioners (F. Wayne Hill WRC) | 2025-04-07 | Gwinnett |  | Non-Outfall | 33070 | Raw Sewage | GA0038130 | Collection System | Blockage Rags wipes,Blockage Tree RootsBlockage Rags wipes,Blockage Tree Roots | Chattahoochee | unnamed trib. crooked creek
Fulton County Department of Public Works (Big Creek WRF) | 2025-04-06 | Fulton |  | Non-Outfall |  |  | GA0024333 |  | Pump Station Mechanical FailurePump Station Mechanical Failure
Dekalb County Department of Watershed Management (Snapfinger Creek AWWTF) | 2025-04-06 | DeKalb |  | Non-Outfall |  | Raw Sewage | GA0024147 | Collection System |  |  | Snapfinger Creek
Cobb County Water System (R.L. Sutton WRF) | 2025-04-03 | Cobb |  | Non-Outfall |  |  | GA0026140 |  | Blockage Rags wipesBlockage Rags wipes
Dekalb County Department of Watershed Management (Snapfinger Creek AWWTF) | 2025-04-03 | DeKalb |  | Non-Outfall |  | Raw Sewage | GA0024147 | Collection System |  |  | SOUTH FORK PEACHTREE CREK
Dekalb County Department of Watershed Management (Snapfinger Creek AWWTF) | 2025-04-02 | DeKalb |  | Non-Outfall | 8 | Raw Sewage | GA0024147 | Collection System
Atlanta, City of (R.M. Clayton, Utoy Creek & South River WRCS) | 2025-04-02 | Fulton | Atlanta | 4033 Stovall Ter NE | 229 | Raw Sewage | GA0039012 | Collection System | debris in the mainline | Chattahoochee | Nancy Creek
Cobb County Water System (R.L. Sutton WRF) | 2025-04-01 | Cobb |  | Non-Outfall |  |  | GA0026140
Dekalb County Department of Watershed Management (Snapfinger Creek AWWTF) | 2025-04-01 | DeKalb |  | Non-Outfall |  | Raw Sewage | GA0024147 | Collection System |  |  | Nancy Creek
Dekalb County Department of Watershed Management (Snapfinger Creek AWWTF) | 2025-04-01 | DeKalb |  | Non-Outfall |  | Raw Sewage | GA0024147 | Collection System |  |  | North Fork Peachtree Creek
Clayton County Water Authority (W.B. Casey WRF & Huie Constructed Wetlands) | 2025-03-31 | Clayton | Forest Park | 5964 Springview Dr. | 10800 | Raw Sewage | GA0038423 | Collection System | Grease blockage caused overflow. | Flint | Jester Creek
Dekalb County Department of Watershed Management (Snapfinger Creek AWWTF) | 2025-03-31 | DeKalb | Atlanta | 2515 Northeast Expressway Atlanta 30345 | 1840 | Raw Sewage | GA0024147 | Collection System | Found manhole 18-205-s307 spilling into North Fork Peachtree Creek due to a grease blockage | Ocmulgee | North Fork Peachtree Creek
Atlanta, City of (R.M. Clayton, Utoy Creek & South River WRCS) | 2025-03-31 | Fulton | Atlanta | 4104 Woodland Park Dr SW | 5000 | Raw Sewage | GA0039012 | Collection System | debris in the mainline | Chattahoochee | Sandy Creek
Dekalb County Department of Watershed Management (Snapfinger Creek AWWTF) | 2025-03-30 | DeKalb | Decatur | 3342 North Druid Rd Decatur 30033 | 0 | Raw Sewage | GA0024147 | Collection System | Found evidence of sewer spilled into Burnt Fork Creek due issue in 4in lateral | Ocmulgee | Burnt Fork Creek
Gainesville, City of (Flat Creek WRF) | 2025-03-28 | Hall | Gainesville | near the 2800 block of Browns Bridge Road | 7200 | Raw Sewage | GA0021156 | Collection System | construction debris | Chattahoochee | unnamed tributary to Flat Creek
Dekalb County Department of Watershed Management (Snapfinger Creek AWWTF) | 2025-03-27 | DeKalb | Tucker | 4259 Drayton Woods Club Tucker 30084 | 99400 | Raw Sewage | GA0024147 | Collection System | Found 15in sewer main broken spilling intermittently into south fork peachtree creek due to structural damage in sewer main between 18-141-s128 and 18-141-s068 | Ocmulgee | South Fork Peachtree Creek
Columbus Water Works (South WRF) | 2025-03-26 | Muscogee | Columbus | 6016 Warm Springs Ct. | 444 | Raw Sewage | GA0020516 | Collection System | Debris caused overflow. | Chattahoochee | Cooper Branch
Macon Water Authority (Rocky Creek WRF) | 2025-03-26 | Bibb | Macon | 2337 Old Clinton Rd. | 2760 | Raw Sewage | GA0024546 | Collection System | Debris and tree limbs in sewer main caused overflow. | Ocmulgee | Walnut Creek
Dekalb County Department of Watershed Management (Snapfinger Creek AWWTF) | 2025-03-25 | DeKalb | Atlanta | 1400 Lake Heam Dr Atlanta 30319 | 37300 | Raw Sewage | GA0024147 | Collection System | Found manhole 18-329-s045 spilling into Nancy Creek due to (wood and rocks) debris |  | Nancy Creek
Dekalb County Department of Watershed Management (Snapfinger Creek AWWTF) | 2025-03-25 | DeKalb | Decatur | 5072 Snapfinger Woods Drive Decatur 30035 | 475 | Raw Sewage | GA0024147 | Collection System | Found evidence of a spill at manhole #16-025-s028 caused by a grease blockage | Ocmulgee | Snapfinger Creek
City of Fairburn | 2025-03-25 | Fulton | Fairburn | 160 Park Way Drive | 148063 | Raw Sewage | GAU060251 | Collection System | The overflow resulted from a blockage caused by rags, disposable towels, and a shirt and flow downstream to a wetland.Blockage Other Debris | Chattahoochee | wetland
Cobb County Water System (R.L. Sutton WRF) | 2025-03-25 | Cobb | Marietta | 3524 Old Suttons Way NE, Marietta, GA 30062 | 2500 | Raw Sewage | GA0026140 | Collection System | Solids | Chattahoochee | Willeo Creek
Macon Water Authority (Rocky Creek WRF) | 2025-03-24 | Bibb | Macon | 851 Wimbish Rd. | 7320 | Raw Sewage | GA0024546 | Collection System | Grease caused overflow | Ocmulgee | Ditch feeding Savage Branch
Walker County Water & Sewer Authority (Walker County WSA WPCP) | 2025-03-24 | Walker |  | Approximately 1000ft North of Glentana Rd. and 50ft West of Dry Creek in Walker Co. | 2000 |  | GA0020478 | WWTP | Blockage in the downstream sewer pipe | Tennessee | Dry Creek
Cobb County Water System (R.L. Sutton WRF) | 2025-03-23 | Cobb | Mableton | 5011 White Blvd Mableton, GA 30126 | 690 | Raw Sewage | GA0026140 | Collection System | Grease | Chattahoochee | Butler Creek
LaFayette, City of (LaFayette WPCP) | 2025-03-23 | Walker | Lafayette | Shattuck Industrial Blvd sewer lift station | 1000 | Raw Sewage | GA0025712 | WWTP | Air relief valve in a manhole at the lift station malfunctioned and a small amount of sewer flowed to the stream. | Coosa | Chattooga Creek
Saint Marys, City of (Point Peter WPCP) | 2025-03-22 | Camden | St. Marys | 100 Ready Street Saint Mary's, Ga. | 30 | Raw Sewage | GA0039047 | Collection System | Broken pipe. | Saint Mary's | Saint Mary's
Jasper, City of (Jasper WPCP) | 2025-03-22 | Pickens | Jasper | At the City of Jasper “Upper 108” sanitary sewer lift station located at 2416 Waleska Hwy in Jasper, GA 30143 | 2000 | Raw Sewage | GA0032204 | WWTP | We believe the station and surrounding area briefly lost utility power and the primary pumps tripped off. When power was restored, neither pump came back online. When our staff arrived, they were able to get the pumps immediately back online. | Coosa | Sharp Mountain Creek
Dekalb County Department of Watershed Management (Snapfinger Creek AWWTF) | 2025-03-22 | DeKalb | Tucker | 4259 Drayton Woods Club Tucker 30084 | 10750 | Raw Sewage | GA0024147 | Collection System | Found manhole 18-140-s210 surcharging due to an unknown blockage in 15in sewer main, causing sewer to spill into South Fork Peachtree Creek through hole in top of 15in sewer main | Ocmulgee | South Fork Peachtree Creek
Atlanta, City of (R.M. Clayton, Utoy Creek & South River WRCS) | 2025-03-22 | Fulton | Atlanta | 169 Woodbine Cir SE | 1230 | Raw Sewage | GA0039012 | Collection System | bypass pump malfunction | Upper Ocmulgee | Sugar Creek
Atlanta, City of (R.M. Clayton, Utoy Creek & South River WRCS) | 2025-03-21 | Fulton | Atlanta | 1299 Gault St SE | 215 | Raw Sewage | GA0039012 | Collection System | leaking mainline | Upper Ocmulgee | Intrenchment Creek
Atlanta, City of (R.M. Clayton, Utoy Creek & South River WRCS) | 2025-03-21 | Fulton | Atlanta | 3195 Roswell Rd NE | 50 | Raw Sewage | GA0039012 | Collection System | collapsed mainline | Chattahoochee | Peachtree Creek
Columbus Water Works (South WRF) | 2025-03-20 | Muscogee | Columbus | 2 Midtown Loop | 214 | Raw Sewage | GA0020516 | Collection System | Debris caused overflow | Chattahoochee | Lindsey Creek
Dekalb County Department of Watershed Management (Snapfinger Creek AWWTF) | 2025-03-20 | DeKalb | Lithonia | 6428 Castle Downs Trace Lithonia 30058 | 300 | Raw Sewage | GA0024147 | Collection System | Found 4in right of way clean out surcharging with evidence of a sewer spill due to a root blockage | Ocmulgee | Swift Creek
Paulding County Board of Commissioners (Coppermine Road WRF) | 2025-03-20 | Paulding | Dallas | 33.95534, -84.76633 Mt. Tabor ridge LS. This is a new LS no address has been assigned to it yet. Located on River Bank Ct. Dallas, Ga. 30132. | 9000 | Raw Sewage | GA0038865 | WWRF | Electric failure of LS. This LS is new and has not been turned over to the county. It is being operated by the contractor. Most of the debris was contained by silt fence and did not enter the creek. | Coosa | Tributary to Possum Creek
Macon Water Authority (Rocky Creek WRF) | 2025-03-20 | Bibb | Macon | 1701 Shurling Dr. | 1360 | Raw Sewage | GA0024546 | Collection System | Broken sewer main caused spill | Ocmulgee | Walnut Creek
Dekalb County Department of Watershed Management (Snapfinger Creek AWWTF) | 2025-03-19 | DeKalb | Atlanta | 2871 Dorby Close Atlanta 30319 | 1680 | Raw Sewage | GA0024147 | Collection System | Found evidence of a spill coming from a contractor's bypass pump spilling into Nancy Creek due to a pump malfunction | Ocmulgee | Nancy Creek
Dekalb County Department of Watershed Management (Snapfinger Creek AWWTF) | 2025-03-19 | DeKalb | Stone Mountain | 4692 East ponce de leon ave stone mountain 30083 | 0 | Raw Sewage | GA0024147 | Collection System | Found private unmapped manhole spilling into the south fork peachtree creek caused by an unknown blockage | Unknown | South Fork Peachtree Creek
Fulton County Department of Public Works (Big Creek WRF) | 2025-03-19 | Fulton | South Fulton | 3737 Thaxton Road South Fulton, GA 30331 | 101885 | Raw Sewage | GA0024333 | Collection System | Line Failure due to erosion | Chattahoochee | Wolf Creek
Macon Water Authority (Rocky Creek WRF) | 2025-03-18 | Bibb | Macon | 1600 Rocky Creek Rd. | 1750 | Raw Sewage | GA0024546 | Collection System | Grease and rags caused blockage. | Ocmulgee | Ditch feeding Rocky Creek
Atlanta, City of (R.M. Clayton, Utoy Creek & South River WRCS) | 2025-03-18 | Fulton | Atlanta | 2239 Meador Ave SE | 486 | Raw Sewage | GA0039012 | Collection System | collapsed mainline | Upper Ocmulgee | South River
Clayton County Water Authority (W.B. Casey WRF & Huie Constructed Wetlands) | 2025-03-17 | Clayton | Riverdale | 637 Briar Hill Ct. | 1800 | Raw Sewage | GA0038423 | Collection System | Pipe failure caused spill | Flint | Flint River
Paulding County Board of Commissioners (Coppermine Road WRF) | 2025-03-17 | Paulding | Dallas | Mt. Tabor ridge LS. This is a new LS no address has been assigned to it yet. Located on River Bank Ct. Dallas, Ga. 30132. | 100000 | Raw Sewage | GA0038865 | WWTP | Electric failure of LS, bypass pump discharge line broke. The bypass pump continued running causing damage to LS pad. This LS is new, and has not been turned over to the county. It is being operated by the contractor Strack. Inc. Most of the debris was contained by silt fence and did not enter the creek. | Coosa | Tributary to Possum Creek
Cartersville, City of (Cartersville WPCP) | 2025-03-16 | Bartow | Cartersville | Plant outfall located adjacent to the Etowah River Canoe/Kayak Launch 34.142592, -84.838454 (via Google Maps) | 155073 |  | GA0024091 | WWTP | Inflow/infiltration during excessive rainfall of approximately 2.0 inches on 03/16/2025. | Coosa | Etowah River
Thomaston, City of (Town Branch WPCP) | 2025-03-16 | Upson | Thomaston | 309 Veterans DriveOutfall | 2700000 |  | GA0030121 | WWTP | Plant hydraulically overloaded | Flint | Town Branch
Fulton County Department of Public Works (Big Creek WRF) | 2025-03-16 | Fulton | South Fulton | 8027 Spence Road South, GA 30218 | 24000 | Raw Sewage | GA0024333 | Collection System | Power/Mechanical Failure at Pump Station | Chattahoochee | Whitewater Creek