## Sheet1
Name of City / Utility: 2016 Validated Water Audit | WSID Number | Service County | Population Served | Volume From Own Sources (Million gallons / Year) | Water Imported (Million gallons / Year) | Water Exported (Million gallons / Year) | Water Supplied (Million gallons / Year) | Billed Metered (Million gallons / Year) | Billed Unmetered (Million gallons / Year) | Unbilled Metered (Million gallons / Year) | Unbilled Unmetered (Million gallons / Year) | Authorized Consumption (Million gallons / Year) | Water Losses (Million gallons / Year) | Apparent Losses (Million gallons / Year) | Real Losses (Million gallons / Year) | Non-Revenue Water (Million gallons / Year) | Length of Mains (miles) | Number of Active and Inactive Service Connections | Average Operating Pressure (psi) | Total Annual Cost of Operating Water System | Customer Retail Unit Cost ( $ / 1000 gallons) | Variable Production Cost | Unavoidable Annual Real Losses (UARL) (Million gallons) | Annual Cost of Apparent Losses | Annual Cost of Real Losses | Value Applied to Real Losses (VPC / CRUC) | Non-Revenue Water as % by Volume of Water Supplied | Non-Revenue Water as % by Cost of Operating System | Apparent Losses per service connection per day | Real Losses per service connection per day | Real Losses per length of main per day | Current Annual Real Losses (CARL) (Million Gallons) | Infrastructure Leakage Index (ILI) | Water Audit Data Validity Score | Priority Area #1 | Priority Area #2 | Priority Area #3 | Grading: Volume From Own Sources | Grading: Volume From Own Sources MMEA | Grading: Water Imported | Grading: Water Imported MMEA | Grading: Water Exported | Grading: Water Exported MMEA | Grading: Billed Metered | Grading: Billed Unmetered | Grading: Unbilled Metered | Grading: Unbilled Unmetered | Grading: Unauthorized Consumption | Grading: Customer Metering Inaccuracies | Grading: Systematic Data Handling Errors | Grading: Length of Mains | Grading: No. of Active and Inactive Service Connections | Grading: Average length of customer service line | Grading: Average Operating Pressure | Grading: Total Annual Cost of Operating Water System | Grading: Customer Retail Unit Cost | Grading: Variable Production Cost | General Comments | FileName | Original Version | Blank | EPD Notes / Comments
Adel | GA0750000 | COOK | 5311 | 306.126 | 0 | 0 | 283.45 | 205.209 | Note 1 | 0.408 | 3.5431 | 209.1601 | 74.2899 | 1.2216 | 73.0682 | 78.241 | 74.2 | 3025 | 54 | 767432 | 2.54 | 2.91 | 16.8554 | 3102.98 | 185593.3 | CRUC | 27.6% | 25.9% | 1.1064 | 66.1775 | N/A | 73.0682 | 4.335 | 55.2124 | Volume from own sources | Unbilled metered | Customer metering inaccuracies | 5 | 2 |  |  |  |  | 7 |  |  | 5 | 5 | 5 | 5 | 5 | 7 | 10 | 3 | 10 | 6 | 5 |  | Adel, City of Worksheet 2015 - updated.xls | 5
Albany Utility Board (Albany) | GA0950000 | DOUGHERTY | 87029 | 4294.02 | 0 | 0 | 4252.7681 | 4054.689 | 0 | 40.664 | 37.606 | 4132.959 | 119.8091 | 104.3473 | 15.4619 | 198.0791 | 610 | 44518 | 55 | 9399350 | 5.31 | 215.79 | 200.3043 | 554084.03 | 3336.52 | VPC | 4.658% | 6.11% | 6.4217 | 0.95155 | N/A | 15.4619 | 0.077192 | 66.4495 | Volume from own sources | Customer metering inaccuracies | Billed metered | 8 | 3 | n/a |  | n/a |  | 5 | n/a | 6 | 6 | 5 | 3 | 5 | 7 | 6 | 10 | 8 | 10 | 6 | 6 |  | Albany Utility Board Worksheet 2015.xls | 5
Alamo | GA3090000 | WHEELER | 3653 | 147.048 | 0 | 0 | 147.048 | 126.3225 | 0 | 0 | 1.8381 | 128.1606 | 18.8874 | 5.9469 | 12.9405 | 20.7255 | 25 | 358 | 45 | 118284.19 | 2.84 | 288.56 | Note 3 | 16889.09 | 3734.11 | VPC | 14.09% | 17.88% | 45.5106 | N/A | 1418.1369 | 12.9405 | Note 3 | 35.0556 | Volume from own sources | Billed metered | Customer metering inaccuracies
Alma | GA0050000 | BACON | 4700 | 227.116 | 0 | 0 | 231.5148 | 140.643 | 0 | 12.517 | 18.84 | 172 | 59.5148 | 3.2628 | 56.252 | 90.8718 | 48 | 1964 | 60 | 317184 | 3.34 | 182.3 | 12.1387 | 10909.41 | 10254.84 | VPC | 39.25% | 8.475% | 4.5515 | 78.47 | N/A | 56.252 | 4.6341 | 58.5726 | Billed metered | Variable production cost (applied to Real Losses) | Customer metering inaccuracies | 9 | 2 | n/a |  | n/a |  | 4 | n/a | 4 | 5 | 5 | 3 | 5 | 5 | 6 | 10 | 3 | 5 | 5 | 5 | QWLA: Alex Wiseman - Registration #0066. Validation date 03/03/2016. Review of performance indicators: normalized apparent & real losses are within expected range, CRUC & VPC costs are on the low end of expected range but acceptable since City has groundwater system, ILI within expected range. | Alma, City of Worksheet 2015.xls | 5
Americus | GA2610000 | SUMTER | 16255 | 907.323 | 0 | 0 | 903.223 | 689.389 | 0 | 0 | 11.2903 | 700.6793 | 202.5437 | 18.0507 | 184.4931 | 213.834 | 146 | 8631 | 80 | 3308288 | 3.11 | 270.5 | 60.8677 | 56063.09 | 49904.83 | VPC | 23.67% | 3.295% | 5.7298 | 58.5634 | N/A | 184.4931 | 3.0311 | 52.137 | Volume from own sources | Customer metering inaccuracies | Billed metered | 6 | 2 | n/a |  | n/a | n/a | 5 | n/a | n/a | 5 | 5 | 3 | 5 | 5 | 6 | 10 | 2 | 5 | 5 | 5 | QWLA No. 0005, Veronica Jarrin | Americus, City of Worksheet 2015.xls | 5
Ashburn | GA2870000 | TURNER | 4178 | 298.586 | 0 | 0 | 351.2776 | 118.713 | 0 | 9.629 | 4.391 | 132.733 | 218.5447 | 7.9298 | 210.6149 | 232.5646 | 45 | 2500 | 45 | 706521 | 2.68 | 242.8 | 10.158 | 21251.91 | 51137.29 | VPC | 66.21% | 10.73% | 8.6902 | 230.8108 | N/A | 210.6149 | 20.7338 | 47.965 | Volume from own sources | Customer metering inaccuracies | Master meter error adjustment
Athens - Clarke County | GA0590000 | CLARKE | 120266 | 4608.64 | 0 | 0 | 4775.7927 | 4158.0991 | Note 1 | 109.3303 | 59.6974 | 4327.1269 | 448.6659 | 65.4401 | 383.2258 | 617.6936 | 820 | 42230 | 90.93 | 7463283.13 | 9.91 | 302.86 | 357.4736 | 648511.17 | 116063.77 | VPC | 12.93% | 10.93% | 4.2455 | 24.8623 | N/A | 383.2258 | 1.072 | 69.7136 | Volume from own sources | Customer metering inaccuracies | Billed metered | 6 | 3 | n/a | 3 | n/a |  | 7 | n/a | 10 | 6 | 5 | 3 | 5 | 10 | 7 | 10 | 5 | 10 | 9 | 10 | Prepared and validated by Marilyn Hall, Athens-Clarke County Public Utilities, QWLA #015 marilyn.hall@athensclarkecounty.com 706-613-3729 | Athens-Clarke 2015 Water Loss Audit.xls | 5
Atlanta - Department of Watershed Management | GA1210001 | FULTON | 650000 | 31361.66 | 4956.42 | 1250.54 | 35032 | 24364 | 13.32 | 0 | 437.9 | 24815.22 | 10216.78 | 2322.3415 | 7894.4385 | 10654.68 | 2816 | 205894 | 103 | 148931861 | 6.34 | 306.88 | 1733.831 | 14716343.73 | 2422645.29 | VPC | 30.41% | 11.6% | 30.9022 | 105.0473 | N/A | 7894.4385 | 4.5532 | 73.8353 | Customer metering inaccuracies | Variable production cost (applied to Real Losses) | Billed metered | 9 | 3 | 9 | 8 | 5 | 3 | 7 | 7 | 8 | 5 | 7 | 5 | 5 | 8 | 6 | 10 | 5 | 8 | 8 | 5 |  | Atlanta, City of Worksheet 2015.xls | 5
Auburn | GA0130000 | BARROW | 6904 | 0 | 191.545 | 0 | 187.7892 | 174.923 | 0 | 0 | 2.3474 | 177.2704 | 10.5189 | 0.90678 | 9.6121 | 12.8662 | 75 | 2842 | 45 | 1382000 | 7.38 | 1200 | 13.6664 | 6692.04 | 11534.48 | VPC | 6.851% | 1.523% | 0.87415 | 9.2662 | N/A | 9.6121 | 0.70333 | 69.7993 | Customer metering inaccuracies | Billed metered | Variable production cost (applied to Real Losses) | n/a |  | 8 | 3 | n/a |  | 6 | n/a | n/a | 5 | 5 | 2 | 5 | 4 | 4 | 10 | 1 | 7 | 8 | 6 | this audit is for the City of Auburn wsid# 0130000, population of 6,887 residents as of the 2010 census located in Barrow county in north east Georgia.The City Of Auburn is a purchase water only system no production or bulk water sales. The system is feed from two points that feed into two elevated tanks then gravity feed to the system. the city is in the process of replaceing all meters and service lines in the city they are currently at 95% replaced. waterloss audit prepared by Elbert Blackstock on behalf of the City Of Auburn.QWLA certified number 0065. information provided by City of Auburn personal and staff from public works and city hall accounting and billing department | Auburn 2015 Waer Audit.xls | 5
Augusta Utilities | GA2450000 | RICHMOND | 204000 | 13265.78 | 0 | 0 | 13000.5684 | 10604.349 | Note 1 | 306.407 | 47.79 | 10958.546 | 2042.0224 | 334.7029 | 1707.3195 | 2396.2194 | 1362.2 | 66927 | 81 | 50573098 | 5 | 225.91 | 514.6838 | 1673514.55 | 385700.55 | VPC | 18.43% | 4.23% | 13.7014 | 69.8909 | N/A | 1707.3195 | 3.3172 | 70.7397 | Volume from own sources | Customer metering inaccuracies | Billed metered | 8 | 3 | n/a |  | n/a |  | 6 |  | 7 | 6 | 5 | 4 | 5 | 6 | 6 | 10 | 9 | 10 | 10 | 9 | Steven Behrend, PE, Augusta Utilities Department Georgia EPD - Qualified Water Loss Auditor No. 0021 February 29, 2016 QWLA Comment: As a quality control measure, the performance indicators have been compared to the filter metrics and fall into range for each one. And regarding Apparent Loss, the result falls to the upper end of the filter range and future measures are planned for 2016 as explained in the customer meter inaccuracies comment. Acknowledgement: This report and the updated commentary below are based upon the 2014 Water Audit report performed by Cavanaugh. | Augusta 2015 Water Audit.xls | 5
Austell Water System | GA0670001 | COBB | 7774 | 0 | 291.85 | 0 | 288.2469 | 124.5062 | 0 | 88.87 | 3.6031 | 216.9792 | 71.2677 | 5.3865 | 65.8812 | 163.7408 | 61 | 3446 | 128 | 885226.38 | 5.51 | 2870 | 39.5676 | 29679.6 | 189078.98 | VPC | 56.81% | 54.69% | 4.2825 | 52.3785 | N/A | 65.8812 | 1.665 | 78.004 | Water imported | Customer metering inaccuracies | Billed metered | n/a |  | 9 | 5 | n/a |  | 7 | n/a | 9 | 5 | 5 | 5 | 5 | 7 | 8 | 10 | 3 | 10 | 9 | 10 | Leak Detection and Repair Plan documentation in place. QWLA Certification by Lorraine Campagne, P.E. (Lcampagne@engineeredhorizons.com; 404-431-5356) - QWLA Registry # 0114. | Austell 2015 Water Audit.xls | 5
Baldwin | GA1370001 | HABERSHAM | 4160 | 688.202 | 0 | 507.513 | 175.2624 | 128.04 | 0.012 | 3.97 | 2.1908 | 134.2128 | 41.0496 | 3.4523 | 37.5973 | 47.2104 | 38.7 | 1675 | 103 | 1655004 | 5.87 | 393 | Note 3 | 20265.22 | 14775.73 | VPC | 26.94% | 2.264% | 5.6468 | 61.4963 | N/A | 37.5973 | Note 3 | 60.2036 | Volume from own sources | Water exported | Customer retail unit cost (applied to Apparent Losses) | 3 | 2 | n/a | n/a | 3 | 2 | 6 | 8 | 3 | 5 | 5 | 9 | 5 | 10 | 3 | 10 | 3 | 10 | 5 | 6 | Mrs. Chris Hinson and Mr Fletcher Holliday performed the water audit certification for the City of Baldwin. Parties that were in attendance and involved in the water audit cerification process were Mr. Jerry Neace Mayor, Mr. Scott Barnhart Public Works Director, Mrs. Janet Van Hook Finance Director, Mrs. Debbie Smith Billing Clerk. Due to the fact that the active and inactive service connection number is 1645 the unavoidable real loss was not calculated and an ILI was not given. | Baldwin City 2015 Water Audit.xls | 5
Baldwin County Water & Sewer | GA0090000 | BALDWIN | 22279 | 0 | 741.357 | 0 | 748.8455 | 462.501 | 0 | 13.886 | 9.3606 | 485.7476 | 263.0979 | 15.2434 | 247.8545 | 286.3445 | 420 | 10000 | 60 | 4119883.87 | 4.5 | 187.47 | 82.6112 | 68595.38 | 46465.28 | VPC | 38.24% | 2.899% | 4.1763 | N/A | 1616.7937 | 247.8545 | 3.0003 | 69.549 | Water imported | Billed metered | Customer metering inaccuracies | n/a | n/a | 8 | 8 | n/a |  | 6 | n/a | 6 | 5 | 5 | 5 | 5 | 3 | 3 | 10 | 1 | 8 | 7 | 10 |  | Baldwin County Water Worksheet 2015 (1-24-17).xls | 5
Bainbridge | GA0870001 | DECATUR | 13546 | 843.241 | 0 | 0 | 843.241 | 669.477 | 0 | 6 | 10.5405 | 686.0175 | 157.2235 | 3.7818 | 153.4417 | 173.764 | 162 | 5550 | 52 | 280000 | 2 | 236.11 | 32.4353 | 7563.59 | 36229.12 | VPC | 20.61% | 17.04% | 1.8669 | 75.7456 | N/A | 153.4417 | 4.7307 | 52.0392 | Volume from own sources | Billed metered | Unbilled metered
Banks County | GA0110026 | BANKS | 6453 | 251.16 | 21.763 | 21.127 | 254.3459 | 197.518 | 0 | 35.087 | 3.1793 | 235.7843 | 18.5616 | 2.2985 | 16.2631 | 56.8279 | 313.4 | 2849 | 99.5 | 1212521.99 | 8.19 | 690.89 | 77.0964 | 18814.02 | 11236.05 | VPC | 22.34% | 4.659% | 2.2104 | N/A | 142.1711 | 16.2631 | 0.21094 | 59.7438 | Volume from own sources | Customer metering inaccuracies | Customer retail unit cost (applied to Apparent Losses) | 5 | 8 | 6 |  | 5 |  | 6 | n/a | 9 | 5 | 7 | 7 | 6 | 6 | 8 | 10 | 2 | 8 | 5 | 5 | We installed 207 Residential meters and one large 10 inch source meter during this audit period. QWLA: Alex Wiseman - Registery # 0066. Validation date 02/25/2016. In 2015, recommend to use new AWWA software, version 5. All required documentation for audit validation was provided by County. All performance indicators exept ILI are within expected ranges. Audit has been double & triple checked without discovery of data error. Reason for ILI below minimum accepted value is unknown at this time. All previous audits also reported low ILI. Converted from 4.2 to v5 | Banks Co 2015 WaterAudit.xls | 4.2
Barnesville | GA1710000 | LAMAR | 6755 | 661.52 | 7.633 | 0 | 662.5277 | 388.646 | 0.20988 | 9.2589 | 22.12 | 420.2347 | 242.293 | 10.7484 | 231.5445 | 273.6718 | 81 | 4096 | 90 | 2182749 | 5.8 | 305.98 | 34.5782 | 62340.96 | 70848 | VPC | 41.31% | 6.542% | 7.1894 | 154.8751 | N/A | 231.5445 | 6.6963 | 74.4212 | Volume from own sources | Billed metered | Customer metering inaccuracies | 8 | 5 | 8 | 2 | n/a |  | 6 | 10 | 8 | 5 | 5 | 6 | 5 | 9 | 9 | 10 | 2 | 8 | 8 | 7 | Brandon Lewis QWLA# 0112: Water audit for the City of Barnesville for the calendar year of 2015. Primary audit preparer, Brandon Lewis. City personnel interviewed: Tammy York, Carolyn Parker, Reggie Watson, Brutz English, Brandon Lewis, Christy Allison, and Niki Sappington. This is the second water audit completed by the City of Barnesville. Validity score improved from 62 in 2014 to a 74 for the 2015 audit year. | Barnesville 2015 Water Audit.xls | 5
Barrow County Water Department | GA0130031 | BARROW | 14043 | 0 | 910.282 | 495.151 | 415.7548 | 379.578 | 0.212 | 3.407 | 5.1969 | 388.3939 | 27.3609 | 9.8044 | 17.5565 | 35.9648 | 155 | 5653 | 91.3 | 3396316.24 | 7.95 | 517.19 | 56.2018 | 77944.6 | 9080.05 | VPC | 8.65% | 2.693% | 4.7517 | 8.5088 | N/A | 17.5565 | 0.31238 | 64.0277 | Customer metering inaccuracies | Customer retail unit cost (applied to Apparent Losses) | Variable production cost (applied to Real Losses) | n/a |  | 5 | 1 | 5 | 1 | 7 | 8 | 6 | 5 | 5 | 2 | 5 | 3 | 6 | 10 | 4 | 5 | 4 | 4 | Robert Sills QWLA #0024 (706) 340-5479 specific comments follow auditors below. In general, please note ILI is below 1 and has been for this utility since 2011. This may be a function of high import/export nature of this system. Increasing validity scores related to import/export data entries may reveil additional water losses. Note the 2014 audit included export volumes. | BARROW COUNTY 2015 WATER AUDIT.xls | 5
Baxley | GA0010000 | APPLING | 5283 | 264.535 | 0 | 0 | 259.348 | 209.303 | Note 1 | 44.016 | 3.2419 | 256.5609 | 2.7872 | 1.1716 | 1.6156 | 50.045 | 108.4 | 3553 | 58 | 587417 | 3.6 | 353.45 | 23.6976 | 4217.86 | 571.02 | VPC | 19.3% | 3.659% | 0.90344 | 1.2458 | N/A | 1.6156 | 0.068174 | 74.1961 | Volume from own sources | Customer metering inaccuracies | Unauthorized consumption | 5 | 7 | n/a |  | n/a |  | 8 | n/a | 6 | 5 | 5 | 5 | 5 | 7 | 5 | 10 | 3 | 8 | 7 | 6 | Note: After completing the audit I added the score manually and it totals 70, but software shows a score of 60. I wondered if that was correct or if there was a glitch in the software. | Baxley Water audit 2015.xls | 5
Big Canoe Subdivision | GA2270004 | PICKENS | 6396 | 248.186 | 5.041 | 0 | 253.227 | 91.525 | 0 | 0.3672 | 3.1653 | 95.0575 | 158.1695 | 4.1948 | 153.9747 | 161.702 | 120 | 2627 | 125 | 1152313 | 17.61 | 992.62 | 47.5983 | 73869.68 | 152838.37 | VPC | 63.86% | 19.98% | 4.3748 | N/A | 3515.4042 | 153.9747 | 3.2349 | 31.2745 | Volume from own sources | Billed metered | Unbilled metered | 3 | 3 | 3 | 1 | n/a |  | 6 | n/a | 9 | 5 | 5 | 3 | 5 | 5 | 3 | 10 | 3 | 10 | 9 | 5 | QWLA: Tal Woodall -- All aduit data was provided and verified by Wesley Parker and Bobby Smallwood. The systems residents are a largely seasonal population and therefore results in large variations in consumption during certain times of the year. The inflated customer retail unit cost is the result of a minumum bill and large decrease consumption for part of the year. The Apparent Losses reported low and may be the result of an over estimation of Real Losses. The ILI reported low but is likely the result of a high CARL and UARL. It is recommended to increase meter accuracy testing at supply meters and field verification of service connections not in use and repair leaks. | Big Canoe Subdivision Worksheet 2015.xls | 5
Blackshear | GA2290000 | PIERCE | 5811 | 178.362 | 0 | 0 | 178.362 | 151.543 | 0.146 | 3.251 | 0.614 | 155.554 | 22.808 | 4.7938 | 18.0142 | 26.673 | 36 | 2242 | 56 | 860367 | 4.01 | 366.71 | 10.8549 | 19223.3 | 6605.97 | VPC | 14.95% | 3.167% | 5.8581 | 22.0133 | N/A | 18.0142 | 1.6595 | 63.4561 | Volume from own sources | Customer retail unit cost (applied to Apparent Losses) | Variable production cost (applied to Real Losses) | 5 | 2 | n/a |  | n/a |  | 8 | 8 | 9 | 8 | 5 | 7 | 6 | 7 | 7 | 10 | 3 | 10 | 5 | 5 | Source meter for well 101 began losing calibration in late June-July of 2015. It was not verified until October when the meter began showing volumes less than 50% of historical flows. The meter stopped working before it could be checked to determine actual % error. There is a known error in readings for volumes pumped during this time. QWLA: Tal Woodall -- All data was provided and verified by Water Operations Specialist, Trey Pearson. Due to the issue with the supply meter it is difficult to make conclusions on loss control based on the data produced by this audit. The utility provided a new meter is on site awaiting installation. It is recommended to test all supply meters, as well as, calibrate and repair or replace as needed. The utilty is advised to review the grading matrix for improvement procedures. | Blackshear, City of Worksheet 2015.xls | 5 |  | Negative ILI value is due to meter inaccuracies.
Blairsville | GA2910000 | UNION | 4035 | 185.103 | 0 | 0 | 183.1977 | 132.407 | 0 | 3.287 | 2.29 | 137.984 | 45.2138 | 4.9857 | 40.228 | 50.7907 | 74 | 1741 | 98 | 657397 | 6.09 | 389 | 23.6615 | 30363.12 | 15648.71 | VPC | 27.72% | 7.329% | 7.8458 | N/A | 1489.3757 | 40.228 | 1.7001 | 58.5946 | Volume from own sources | Unbilled metered | Customer metering inaccuracies | 5 | 3 | n/a |  | n/a |  | 7 | n/a | 3 | 5 | 5 | 4 | 5 | 10 | 7 | 10 | 3 | 10 | 5 | 10 | Audit validaiton performed by Fletcher Holliday and Chris Hinson. In attendance from City: Water Distribution Superintendent and his assistant, Water Plant Superintendent and his assistant, Mayor, Untility Billing Clerks, and Finance Officer. | Blairsville 2015 Water Audit.xls | 5
Blakely | GA0990000 | EARLY | 4855 | 373.974 | 0 | 0 | 373.974 | 192.657 | 0 | 3.886 | 4.6747 | 201.2177 | 172.7563 | 5.4277 | 167.3287 | 181.317 | 54 | 2666 | 65 | 377863 | 4.11 | 40.67 | 16.4186 | 22307.68 | 6805.26 | VPC | 48.48% | 7.797% | 5.5778 | 171.956 | N/A | 167.3287 | 10.1914 | 50.7647 | Volume from own sources | Billed metered | Customer metering inaccuracies | 4 | 2 | n/a |  | n/a |  | 3 | n/a | 9 | 5 | 5 | 1 | 5 | 3 | 7 | 10 | 2 | 9 | 6 | 4 | QWLA: Tal Woodall -- All data was provided and verified by Water Treatment Supervisor Adam Askew. The performance indicators suggest an unknown degree of error in the data provided. The Apparent losses reported very low while the Real Losses and ILI both reported very high values. This is most likely due an under registered billed metered volume, over registered supply volume, or both. However, the later is less likely to occur in normal operation. It is recommended to implement a customer meter testing and replacement program to insure an accurate meter population. It is also recomended to have the source meters tested for accuracy annually. It is also recomnded to review/ update billing policies and procedures as necessary. | Blakely, City of Worksheet 2015.xls | 5
Blue Ridge Water & Sewer | GA1110000 | FANNIN | 6112 | 284.94 | 0 | 6.78 | 281.0719 | 159.8802 | 0 | 0.8 | 1e-07 | 160.6802 | 120.3918 | 9.4525 | 110.9393 | 121.1918 | 122 | 3553 | 110 | 2297481.59 | 7.66 | 534.17 | 47.8977 | 72358.69 | 59260.43 | VPC | 43.12% | 5.747% | 7.2888 | N/A | 2491.3379 | 110.9393 | 2.3162 | 66.9312 | Volume from own sources | Unbilled metered | Billed metered | 7 | 2 | n/a | 3 | 5 | 1 | 7 | n/a | 5 | 5 | 5 | 7 | 5 | 5 | 5 | 10 | 3 | 7 | 8 | 7 | QWLA : REBECCA HARKINS #0072 706-632.2091 rharkins@cityofblueridgega.gov - The City is working hard on its water loss control program. 6 new zone meters were installed in 2015, 20% of the customer meters were replaced. A leak survey was conducted by a 3rd party, which surveyed 41.6 miles of pipe. New leak detection equipment was purchased for daily use. Records indicate that the City reduced its 2015 non-revenue water by almost 37 MG compared to 2014. | Blue Ridge 2015 WATER AUDIT.xls | 5
Bowdon Water System | GA0450000 | CARROLL | 6045 | 195.13 | 1.389 | 0 | 202.6118 | 135.886 | 0 | 8.776 | 11.741 | 156.403 | 46.2088 | 6.0931 | 40.1158 | 66.7258 | 140 | 2420 | 77 | 829070 | 6.19 | 316.33 | 31.4888 | 37716 | 12689.82 | VPC | 32.93% | 6.863% | 6.8981 | N/A | 785.0444 | 40.1158 | 1.274 | 52.5484 | Volume from own sources | Billed metered | Unbilled metered | 3 | 2 | n/a |  | n/a |  | 5 | n/a | 5 | 5 | 5 | 6 | 5 | 2 | 4 | 10 | 3 | 6 | 5 | 5 | City of Bowdon, Georgia Water Audit and Level 1 Validation. Water System ID 0450000. Bobby C. Elliott, P.E., City Manager preparing and certifying the audit. QWLA Certification # 0166. Assume all comments are preparer/QWLA related specifically to operations and or observations. Frank Carlson - Water Plant Superintendent; Tim Keeton- Public Works Director; Susan Pierce- City Clerk and Jan Gibbs - Account Receivables/Payables clerk help provide data and support documents for this audit. QWLA Training has improved how this task was performed. | Bowdon 2015 Water Audit.xls | 5
Braselton Water System | GA1570000 | JACKSON | 11443 | 218.795 | 345.842 | 4.855 | 548.8059 | 521.867 | 0 | 14.595 | 6.8601 | 543.3221 | 5.4838 | 19.2683 | -13.7845 | 26.9389 | 120 | 5220 | 112 | 2747812.18 | 7.92 | 4198.29 | 58.5483 | 152604.86 | -57871.25 | VPC | 4.909% | 6.726% | 10.113 | -7.2348 | N/A | -13.7845 | -0.23544 | 53.6863 | Water imported | Volume from own sources | Unbilled metered | 5 | 3 | 5 | 3 | 9 | 5 | 5 | n/a | 3 | 5 | 5 | 3 | 5 | 10 | 5 | 10 | 4 | 10 | 5 | 7 | Water audit certification performed by Fletcher Holliday and Chris Hinson. Town personnel in attendance for audit verification: Public Utilities Director (PUD) and Utility Billing Clerk. Please see comment in unbilled metered for explanation of ILI and the apparent water loss value. | Braselton 2015 Water Audit.xls | 5 |  | Negative ILI value is due to meter inaccuracies.
Bremen | GA1430000 | HARALSON | 6200 | 86.48 | 276.797 | 71.593 | 290.9094 | 227.148 | 0 | 1.8 | 3.6364 | 232.5844 | 58.325 | 5.9676 | 52.3574 | 63.7614 | 75 | 3177 | 90 | 1158829 | 5.4 | 932.43 | 28.9836 | 32224.78 | 48819.64 | VPC | 21.92% | 7.431% | 5.1462 | 45.1511 | N/A | 52.3574 | 1.8065 | 78.3928 | Variable production cost (applied to Real Losses) | Unauthorized consumption | Systematic data handling errors | 5 | 5 | 9 | 3 | 9 | 3 | 9 | n/a | 9 | 5 | 5 | 8 | 5 | 8 | 7 | 10 | 5 | 8 | 9 | 4 | QWLA: Tal Woodall -- All components of this audit were provided and verified by Utility Superintednent Mike Thompson. The perforamnce indicators are on the lower end of their expected ranges. This is supprted by the utilites proactive water loss control practices. | Bremen, City of Worksheet 2015.xls | 5
Brunswick - Glynn County Joint W & S Commission - (City of Brunswick & North Mainland Combined) | GA1270000 | GLYNN | 43998 | 1779.511 | 0 | 0 | 1782.8985 | 1383.425 | 0 | 139 | 22.2862 | 1544.7112 | 238.1873 | 9.2872 | 228.9001 | 399.4735 | 323.5 | 19899 | 54 | 2703478 | 2.51 | 193.49 | 93.3266 | 23310.94 | 44289.87 | VPC | 22.41% | 3.655% | 1.2787 | 31.5153 | N/A | 228.9001 | 2.4527 | 69.4636 | Volume from own sources | Customer metering inaccuracies | Billed metered | 7 | 3 | n/a |  | n/a |  | 5 | n/a | 10 | 5 | 5 | 3 | 5 | 9 | 6 | 10 | 3 | 10 | 10 | 7 | John D. Donaghy, CPA,CMA - Director of Finance and Administration - Qualified Water Loss Auditor Registry No. 0043 William O. Simmons, Jr. - Superintendent of Water Production | Brunswick 2015 Water Audit.xls | 5
Brunswick - Glynn County Joint W & S Commission - St Simons | GA1270001 | GLYNN | 23579 | 1025.345 | 0 | 0 | 1029.773 | 821.788 | 0 | 123.246 | 12.8722 | 957.9062 | 71.8669 | 5.4802 | 66.3867 | 207.985 | 145.85 | 11638 | 53 | 1557731 | 2.38 | 198.4 | 49.0347 | 13042.87 | 13171.04 | VPC | 20.2% | 3.416% | 1.2901 | 15.6282 | N/A | 66.3867 | 1.3539 | 72.278 | Volume from own sources | Customer metering inaccuracies | Billed metered | 7 | 3 | n/a |  | n/a |  | 5 | n/a | 10 | 5 | 5 | 3 | 5 | 4 | 6 | 10 | 3 | 10 | 10 | 7 | John D. Donaghy, CPA,CMA - Director of Finance and Administration - Qualified Water Loss Auditor Registry No. 0043 William O. Simmons, Jr. - Superintendent of Water Production | St Simons Island 2015 Water Audit.xls | 5
Brunswick - Glynn County Joint W & S Commission - South Mainland | GA1270150 | GLYNN | 2072 | 107.164 | 0 | 0 | 108.2027 | 96.497 | 0 | 3.681 | 1.3525 | 101.5305 | 6.6722 | 0.60199 | 6.0702 | 11.7057 | 46.8 | 1567 | 56 | 162806 | 2.61 | 193.49 | 9.9796 | 1571.2 | 1174.53 | VPC | 10.82% | 2.285% | 1.0525 | 10.6131 | N/A | 6.0702 | 0.60826 | 63.2394 | Volume from own sources | Customer metering inaccuracies | Billed metered
Buford | GA1350000 | GWINNETT | 8045 | 448.47 | 24.836 | 0 | 482.4584 | 368.201 | 1.98 | 6.601 | 6.0307 | 382.8127 | 99.6457 | 24.0237 | 75.622 | 112.2774 | 74 | 3417 | 61 | 1896061.55 | 2.07 | 506.47 | 20.3255 | 49729.11 | 38300.27 | VPC | 23.27% | 4.98% | 19.2621 | 60.6332 | N/A | 75.622 | 3.7205 | 53.8254 | Volume from own sources | Customer metering inaccuracies | Billed metered | 5 | 2 | 2 |  | n/a |  | 5 | 6 | 8 | 5 | 5 | 2 | 6 | 3 | 5 | 10 | 2 | 10 | 5 | 5 | QWLA: Cory Burge #0113 ILI and Losses are in line with the limited resources dedicated to proactive leak detection. More accurate methods were used in calculating weighted averages and VPC. Audit follows expected trends from previous years. | Buford 2015 Water Audit.xls | 5
Butler | GA2690000 | TAYLOR | 2948 | 176.261 | 0 | 0 | 176.261 | 154.287 | 0.6336 | 1.102 | 2.2033 | 158.2259 | 18.0351 | 3.1927 | 14.8424 | 21.3404 | 37.9 | 1550 | 60 | 392450 | 3.09 | 453.13 | Note 3 | 9865.44 | 6725.55 | VPC | 12.11% | 4.609% | 5.6433 | 26.235 | N/A | 14.8424 | Note 3 | 52.693 | Volume from own sources | Billed unmetered | Customer metering inaccuracies | 3 | 2 | n/a |  | n/a |  | 8 | 6 | 7 | 5 | 5 | 6 | 5 | 3 | 4 | 10 | 4 | 8 | 7 | 6 | QWLA: Tal Woodall -- All inputs and grading were provided and verified by Public Work Director, David Windham. The software was unable to calculate the UARL and ILI based on the data provided. This water system serves a prison population, on a single compund metere, which places them over the 3,300 servered threshold. The Apparent and Real Losses both reported low. This is expected due to the utilies loss control practices, however, these indicators may be somewhat under-stated based on the lack of supply meter testing. The utilty has been unable to test there supply meters due to the design of the pumping facilities. It is recommended to review data management and policies and procudes and update as needed. | Butler, City of Worksheet 2015.xls | 5
Butts County WSA/Jackson/Jenkinsburg | GA0350051 | BUTTS | 22500 | 870.57 | 12.475 | 72.571 | 765.4821 | 717.716 | 0 | 2.713 | 9.5685 | 729.9975 | 35.4846 | 7.3282 | 28.1564 | 47.7661 | 275 | 8242 | 84.39 | 3179977 | 4.92 | 766.87 | 83.9071 | 36054.95 | 21592.28 | VPC | 6.24% | 2.109% | 2.436 | N/A | 280.5119 | 28.1564 | 0.33557 | 69.074 | Unbilled metered | Volume from own sources | Variable production cost (applied to Real Losses) | 7 | 2 | 9 | 1 | 9 | 1 | 7 | n/a | 9 | 5 | 5 | 7 | 5 | 7 | 9 | 10 | 9 | 10 | 8 | 5 | Auditor: All information taken from direct source documents of the Butts County, et al. Water & Sewer Authority, the City of Jackson, and the City of Jenkinsburg. Source information documentation is available for review in separate Excel and .pdf files. | Butts County 2015 Water Audit.xls | 5
Byron | GA2250000 | PEACH | 6419 | 292.369 | 0 | 0 | 289.4743 | 232.766 | 0 | 1.1508 | 3.6184 | 237.5352 | 51.939 | 8.5401 | 43.3989 | 56.7083 | 81 | 3235 | 60 | 446085.5 | 4 | 338.84 | 20.2238 | 34160.56 | 173595.55 | CRUC | 19.59% | 50.85% | 7.2327 | 36.7546 | N/A | 43.3989 | 2.1459 | 47.8673 | Volume from own sources | Customer metering inaccuracies | Variable production cost (applied to Real Losses) | 4 | 2 | n/a |  | n/a |  | 5 | n/a | 7 | 5 | 5 | 3 | 5 | 5 | 3 | 10 | 2 | 5 | 5 | 4 | Audit Prepared by Chad Smith and Lauren Mitchell. QWLA: Chad Smith | Byron 2015 WATER AUDIT.xls | 5
Cairo | GA1310000 | GRADY | 9469 | 516.015 | 0 | 0 | 498.5652 | 353.965 | Note 1 | Note 1 | 6.2321 | 360.1971 | 138.3682 | 3.0185 | 135.3497 | 144.6002 | 120 | 4200 | 67 | 1057538.41 | 1.65 | 471.44 | 31.2828 | 4980.45 | 63809.26 | VPC | 29% | 6.783% | 1.969 | 88.2907 | N/A | 135.3497 | 4.3266 | 65.2072 | Volume from own sources | Customer retail unit cost (applied to Apparent Losses) | Variable production cost (applied to Real Losses) | 6 | 3 | n/a | n/a | n/a |  | 8 | n/a | n/a | 5 | 5 | 4 | 5 | 4 | 5 | 10 | 5 | 10 | 5 | 5 |  | Cairo 2015 Water Audit.xls | 5
Calhoun | GA1290000 | GORDON | 49088 | 3592.164 | 0 | 620.38 | 2932.1455 | 2524.474 | Note 1 | Note 1 | 36.6518 | 2561.1258 | 371.0197 | 81.03 | 289.9897 | 407.6715 | 841 | 20944 | 104 | 9094476 | 2.6 | 255.95 | 291.9659 | 210677.93 | 74222.87 | VPC | 13.9% | 3.236% | 10.5997 | N/A | 944.6996 | 289.9897 | 0.99323 | 80.5904 | Variable production cost (applied to Real Losses) | Customer retail unit cost (applied to Apparent Losses) | Volume from own sources | 9 | 3 |  |  | 10 | 10 | 10 | n/a | n/a | 5 | 5 | 9 | 5 | 7 | 6 | 10 | 9 | 10 | 6 | 5 | QWLA: Kyle Ellis #0082 Initial checks: seem to be appropriate; real losses > apparent / non-revenue < 100% system cost / apparent losses is 7.95 / customer retail unit cost $2.45/ variable production cost $256.81/ ILI of 0.67 appears low. Final Checks:real losses > apparent / non-revenue < 100% system cost / apparent losses is 6.81 / customer retail unit cost $2.45/ variable production cost $256.81/ ILI of 3.39 seems to be within acceptable ranges. | Calhoun 2015 Water Audit.xls | 5
Camilla | GA2050001 | MITCHELL | 5922 | 1328.416 | 0 | 0 | 1328.416 | 997.328 | 4.51 | 0 | 16.6052 | 1018.4432 | 309.9728 | 47.3697 | 262.6031 | 326.578 | 71 | 2657 | 54 | 2902055 | 6.1 | 267.45 | 15.4262 | 288955.13 | 70233.2 | VPC | 24.58% | 12.53% | 48.8446 | 270.7793 | N/A | 262.6031 | 17.0232 | 50.8333 | Volume from own sources | Customer metering inaccuracies | Billed metered | 5 |  | n/a |  | n/a |  | 6 | 7 | 10 | 5 | 5 | 3 | 5 | 4 | 6 | 4 | 8 | 8 | 6 | 6 |  | Camilla, City of Worksheet 2015.xls | 5
Canton | GA0570001 | CHEROKEE | 14300 | 1108.42 | 67.785 | 77.204 | 1121.4296 | 739.812 | Note 1 | 5.724 | 14.0179 | 759.5539 | 361.8757 | 19.8681 | 342.0076 | 381.6176 | 148 | 7900 | 80 | 4749116 | 6.97 | 547.72 | 57.9819 | 138480.83 | 187324.4 | VPC | 34.03% | 7.088% | 6.8903 | 118.6085 | N/A | 342.0076 | 5.8985 | 66.7748 | Volume from own sources | Customer retail unit cost (applied to Apparent Losses) | Variable production cost (applied to Real Losses) | 8 | 5 | 5 | 5 | 5 | 5 | 5 | n/a | 9 | 5 | 5 | 3 | 5 | 7 | 6 | 10 | 5 | 10 | 5 | 5 | QWLA = Pedro Rossello, P.E. - Engineering Strategies, Inc. - prossello@esi-ga.com - 770-429-0001 City of Canton preparer = David Hatabian, P.E. - City Engineer - david.hatabian@canton-georgia.com - 770-704-1513 QWLA received copy of 2014 Water Audit and compared to 2015 data - no red flags. City states data prior to 2014 were not as reliable. | Canton 2015 Water Audit.xls | 5
Carroll County Water Authority | GA0450001 | CARROLL | 48941 | 1989.596 | 4.558 | 649.801 | 1427.3528 | 1055.089 | 0 | 8.501 | 17.8419 | 1081.4319 | 345.9209 | 16.9494 | 328.9714 | 372.2638 | 771.9 | 18710 | 99.91 | 7236220 | 7.02 | 367.43 | 254.6311 | 118985.05 | 120873.97 | VPC | 26.08% | 3.448% | 2.4819 | N/A | 1167.6274 | 328.9714 | 1.292 | 70.5769 | Customer metering inaccuracies | Water exported | Variable production cost (applied to Real Losses) | 5 | 3 |  |  | 7 | 1 | 7 | n/a | 6 | 5 | 5 | 3 | 5 | 1 | 7 | 10 | 9 | 10 | 10 | 5 |  | Carroll County 2015 Water Audit- Corrected Copy (7-22-16).xls | 5
Carrollton | GA0450002 | CARROLL | 25200 | 1799.71 | 0 | 1.3763 | 1798.3337 | 1438.2821 | 0 | 36.1927 | 22.4792 | 1496.954 | 301.3797 | 22.9852 | 278.3945 | 360.0516 | 241.73 | 10773 | 75 | 4266342.44 | 4.23 | 2.37 | 80.0365 | 97227.5 | 659.79 | VPC | 20.02% | 2.298% | 5.8455 | 70.7996 | N/A | 278.3945 | 3.4783 | 80.4251 | Volume from own sources | Billed metered | Customer metering inaccuracies | 9 | 3 | n/a |  | n/a |  | 7 | n/a | 10 | 5 | 5 | 6 | 5 | 10 | 10 | 10 | 7 | 10 | 9 | 5 |  | Carrollton Water Audit 2015.xls | 5
Cartersville Water Department | GA0150002 | BARTOW | 24830 | 4351.45 | 0 | 2075.122 | 2153.792 | 1728.639 | 0 | 0 | 26.9224 | 1755.5614 | 398.2306 | 63.1691 | 335.0614 | 425.153 | 230 | 11351 | 85 | 4215193 | 1.59 | 150.23 | 91.4291 | 134267.32 | 50336.28 | VPC | 19.74% | 4.475% | 15.2468 | 80.8719 | N/A | 335.0614 | 3.6647 | 61.621 | Volume from own sources | Water exported | Customer metering inaccuracies | 5 | 5 | n/a |  | 5 | 3 | 7 | n/a | n/a | 5 | 5 | 5 | 5 | 10 | 5 | 10 | 4 | 10 | 8 | 5 | QWLA: Sidney Forsyth #0095 I audited using 10 step method and reviewed source documents. Slight data adjustments were made within source documents and applied to final audit. I concur with final data entries and scores. [CRUC converted: $/100 cubic feet (ccf) to $/1000 gallons (US)] | Cartersville 2015 Water Audit.xls | 5
Catoosa Utility District | GA0470000 | CATOOSA | 50994 | 1594 | 389 | 87 | 1913.3396 | 1526 | Note 1 | Note 1 | 23.9167 | 1549.9167 | 363.4228 | 24.0125 | 339.4103 | 387.3396 | 538 | 22212 | 113 | 4925576 | 2.98 | 325.08 | 257.467 | 71557.22 | 110335.52 | VPC | 20.24% | 3.851% | 2.9618 | 41.8644 | N/A | 339.4103 | 1.3183 | 73.7631 | Volume from own sources | Unauthorized consumption | Systematic data handling errors | 5 | 5 | 8 | 5 | 5 | 5 | 5 | n/a | n/a | 5 | 5 | 7 | 5 | 9 | 9 | 10 | 9 | 10 | 10 | 9 | QWLA= Charles Reynolds 0148. All comments in Red was by QWLA. All other is from auditor. | Catoosa Utility District Auth Worksheet 2015.xls | 5
Cave Spring | GA1150000 | FLOYD | 4180 | 321.305 | 0 | 117.454 | 182.7291 | 83.339 | 0.024 | 5.787 | 2.2841 | 91.4341 | 91.295 | 2.7167 | 88.5784 | 99.3661 | 87 | 1628 | 118 | 930763.43 | 4.02 | 187.92 | 30.7895 | 10920.99 | 16645.65 | VPC | 54.38% | 3.125% | 4.5718 | N/A | 2789.4305 | 88.5784 | 2.8769 | 58.5968 | Volume from own sources | Customer metering inaccuracies | Billed metered | 6 | 3 | n/a | n/a | 2 | 1 | 5 | 7 | 5 | 5 | 5 | 3 | 5 | 3 | 4 | 10 | 3 | 7 | 7 | 4 | QWLA Denise Ferguson # 0162 - Fiscal Year is July 2014 - June 2015. All information was derived from Calendar year 2015. Checked all units input match. Person completing the audit and the QWLA are the same. ILI is up from last year due to better understanding of audit and data being tracked. | Cave Spring 2015 Water Audit.xls | 5
Cedartown | GA2330000 | POLK | 9750 | 634.46 | 0 | 0 | 635.46 | 363.037 | 0 | 60.34 | 7.9433 | 431.3202 | 204.1398 | 13.3521 | 190.7877 | 272.423 | 85.9 | 4047 | 86 | 882149 | 2.77 | 176.47 | 33.6428 | 36985.21 | 33668.3 | VPC | 42.87% | 9.375% | 9.039 | 129.1589 | N/A | 190.7877 | 5.671 | 69.0117 | Volume from own sources | Customer metering inaccuracies | Customer retail unit cost (applied to Apparent Losses) | 7 | 2 | n/a |  | n/a |  | 5 | n/a | 3 | 5 | 5 | 4 | 5 | 2 | 7 | 10 | 2 | 5 | 6 | 5 | QWLA: Tal Woodall --All supporting documents, inputs, and comments were reviewed and verified with Water Superintendent Donna Atkins. The performance indicators are all with in the expect ranges and on the mid-to-low end of each range . This is supported by age of the infrustructure and metering practices, however; an increase in meter accuracy testing is suggested. | Cedartown Water Audit 2015.xls | 5
Centerville | GA1530000 | HOUSTON | 9821 | 416.242 | 9.377 | 0 | 460.361 | 336.408 | 0 | 7.418 | 5.7545 | 349.5805 | 110.7805 | 12.6257 | 98.1548 | 123.953 | 48 | 4663 | 65 | 2090451.38 | 3.59 | 245.62 | 22.7554 | 45326.32 | 24108.77 | VPC | 26.93% | 3.476% | 7.4182 | 57.6704 | N/A | 98.1548 | 4.3135 | 55.8199 | Volume from own sources | Unbilled metered | Customer metering inaccuracies | 5 | 2 | 3 | 1 | n/a |  | 7 | n/a | 5 | 5 | 5 | 5 | 5 | 7 | 7 | 10 | 3 | 10 | 5 | 5 | Prepared by: Betty Chamberlain / Office Manager / cwd500@centerville.mgacoxmail.com / 478-953-3222 QWLA: Tal Woodall -- All inputs, grading, and comments were verified with Betty Chamberlain and Water Superintendent, Mike Brumfield. Accuracy test results for finished water meters at the Archdale and Surry treatment plants reported 47.4% and 86.8%, respectively. The Archdale meter has been replaced and there are plans to have the Surry meter replaced in the near future. The data from the new meter, although limited, has yet to support the inaccuracy found by the meter test. It is recommended to have the new Archdale meter tested and the Surry meter tested once it has been replaced to insure their accuracy. It was also suggested to consult the meter test company if the production values do not increase with the new meters in place. The resulting ILI is very high and is expected to improve with meter replacement and continued loss control improvements. The Apparent losses are on the low end of the range and may be under-estimated. It is recommended to increase metering on unbilled consumption such as flushing. The Real Losses reported in the mid-to-high range and should also improve with increased metering and continued meter change out program. | Centerville, City of Worksheet 2015.xls | 5
Chatsworth Water Works Commission | GA2130000 | MURRAY | 28262 | 563.427 | 540.239 | 0.213 | 1114.6011 | 842.5542 | 0 | 18.7865 | 13.9325 | 875.2732 | 239.328 | 13.5933 | 225.7347 | 272.047 | 419.24 | 11130 | 93.8 | 4298604.51 | 5.94 | 714.55 | 134.8112 | 80744.2 | 161298.7 | VPC | 24.41% | 6.175% | 3.3461 | N/A | 1475.1721 | 225.7347 | 1.6745 | 73.4456 | Volume from own sources | Water imported | Billed metered | 7 | 5 | 7 | 3 | 7 | 6 | 7 | n/a | 9 | 5 | 5 | 6 | 5 | 10 | 8 | 10 | 5 | 10 | 9 | 10 | QWLA: Brian Skeens, #0000 | Chatsworth Water Works Commission Worksheet 2015.xls | 5
Chattooga County Water District | GA0550000 | CHATTOOGA | 7306 | 325.246 | 0 | 11.679 | 305.2549 | 188.062 | Note 1 | Note 1 | 3.8157 | 191.8777 | 113.3772 | 5.0713 | 108.306 | 117.1929 | 300 | 3967 | 65 | 1465074 | 6.1 | 263.54 | 52.6232 | 30934.88 | 660666.31 | CRUC | 38.39% | 48.79% | 3.5024 | N/A | 989.0955 | 108.306 | 2.0581 | 52.3107 | Volume from own sources | Customer retail unit cost (applied to Apparent Losses) | Variable production cost (applied to Real Losses) | 3 | 3 |  |  |  |  | 7 |  |  | 5 | 5 | 7 | 5 | 6 | 4 | 10 | 4 | 7 | 4 | 6 |  | Chattooga County Worksheet 2015.xls | 5
Cherokee County Water & Sewerage Authority | GA0570002 | CHEROKEE | 177870 | 6299.88 | 28.174 | 403.904 | 6085.0981 | 5134.515 | 0 | 164.326 | 0.544 | 5299.385 | 785.7131 | 75.4928 | 710.2203 | 950.5831 | 1263.91 | 66602 | 111 | 34175529 | 5.61 | 247.48 | 681.7886 | 423514.68 | 175765.33 | VPC | 15.62% | 1.873% | 3.1055 | 29.2155 | N/A | 710.2203 | 1.0417 | 82.378 | Volume from own sources | Unauthorized consumption | Variable production cost (applied to Real Losses) | 9 | 2 | 3 | 1 | 9 | 3 | 6 | n/a | 9 | 9 | 5 | 7 | 5 | 9 | 7 | 10 | 1 | 10 | 9 | 7 | QWLA Jennifer Arp: #0091 | Cherokee County Water & Sewerage Auth Worksheet 2015.xls | 5
Chickamauga | GA2950000 | WALKER | 4150 | 334.2685 | 0.149 | 0 | 352.0132 | 136.548 | 0.002 | 19.607 | 4.4002 | 160.5572 | 191.456 | 4.4082 | 187.0478 | 215.4632 | 41.9 | 2024 | 165 | 360912.48 | 2.94 | 272.29 | 31.9361 | 12960.22 | 50931.24 | VPC | 61.21% | 19.51% | 5.9671 | 253.1916 | N/A | 187.0478 | 5.8569 | 56.386 | Volume from own sources | Billed metered | Unbilled metered | 2 | 5 | 3 | 4 | n/a | 3 | 3 | 8 | 9 | 5 | 5 | 1 | 5 | 4 | 3 | 10 | 2 | 10 | 6 | 10 | Water Audit certified by Carlos R. Haney QWLA # 0158. After reviewing Water Audit conducted by Debbie Gossett. had meeting with Debbie Gossett and City manager Micheal Haney about putting a leak detection program in to policy and implementing it with in the next year. Also re-evaluating policy on City school water use. | Chickamauga, City of Worksheet 2015.xls | 5
Clarkesville | GA1370002 | HABERSHAM | 5785 | 206.458 | 0.045 | 0 | 201.526 | 142.0023 | Note 1 | 14.2032 | 2.5191 | 158.7246 | 42.8014 | 2.4367 | 40.3647 | 59.5237 | 60.6 | 2320 | 81.3 | 1356457.66 | 5.07 | 352.53 | 20.0554 | 12353.84 | 14229.77 | VPC | 29.54% | 2.394% | 2.8775 | 47.6673 | N/A | 40.3647 | 2.0127 | 67.849 | Volume from own sources | Customer metering inaccuracies | Unbilled metered | 6 | 3 |  |  |  |  | 7 |  | 5 | 5 | 5 | 4 | 5 | 5 | 5 | 10 | 3 | 9 | 9 | 5 | QWLA- Nancy W. Gosnell #0169. Assisted by Public Services Superintendent (Jeremy Garmon), Billing Clerk (Sandy Forrester), Special Projects Director (Tim Durham), and City of Cornelia, Public Utilities Director (Keith Ethridge). A proactive leak detection of complete system was performed in 2013 and repairs made. | Clarkesville Water Audit 2015.xls | 5
Clayton | GA2410000 | RABUN | 7225 | 0 | 437.427 | 41.337 | 396.09 | 185.919 | Note 1 | 1.536 | 4.9511 | 192.4061 | 203.6839 | 11.3211 | 192.3628 | 210.171 | 135 | 3650 | 160 | 1840502.9 | 8.91 | 2150 | 76.8973 | 100870.78 | 413580.02 | VPC | 53.06% | 28.71% | 8.4977 | N/A | 3903.862 | 192.3628 | 2.5016 | 57.6471 | Water imported | Customer metering inaccuracies | Billed metered |  | 2 | 5 | 3 | n/a |  | 6 | 7 | 7 | 5 | 5 | 4 | 5 | 8 | 6 | 5 | 3 | 8 | 8 | 6 |  | Clayton, City of Worksheet 2015.xls | 5
Clayton County Water Authority | GA0630000 | CLAYTON | 270000 | 9411.334 | 0 | 514.131 | 8888.4623 | 8318.966 | 16.709 | 92.419 | 111.1058 | 8539.1998 | 349.2626 | 43.8343 | 305.4282 | 552.7873 | 1368.38 | 85039 | 60 | 31677011 | 5.68 | 418.15 | 441.4774 | 248978.94 | 127714.81 | VPC | 6.219% | 1.458% | 1.4122 | 9.8401 | N/A | 305.4282 | 0.69183 | 82.6289 | Customer metering inaccuracies | Volume from own sources | Unauthorized consumption | 8 | 8 | 10 | n/a | 10 | 7 | 9 | n/a | 8 | 5 | 5 | 8 | 5 | 10 | 10 | 10 | 5 | 9 | 9 | 8 |  | Clayton County Water Auth Worksheet 2015.xls | 5
Cleveland | GA3110000 | WHITE | 4906 | 171.624 | 56.087 | 0 | 227.711 | 174.897 | 0 | 0.367 | 2.8464 | 178.1104 | 49.6006 | 2.7769 | 46.8237 | 52.814 | 40 | 2181 | 90.7 | 1349153.58 | 4.86 | 916.09 | 17.9945 | 13495.56 | 227563.42 | CRUC | 23.19% | 19.02% | 3.4882 | 58.819 | N/A | 46.8237 | 2.6021 | 46.2536 | Volume from own sources | Billed metered | Unbilled metered | 3 | 2 | 3 | 2 | n/a |  | 5 | n/a | 5 | 5 | 5 | 3 | 5 | 5 | 7 | 10 | 3 | 10 | 8 | 8 | QWLA: Tal Woodall -- All dta was provided and verified by Water Superintendent, Tom Guy. The Apparent Losses, Real Losses, and ILI all reported on the low end of the respective ranges. These indicators may be under-stated due to the lack of meter testing. It is recommended to test all supply meter where acess is available and replace or repair suspected malfuctioning meters. The utility has obtained testing equipment for retail meters and plans to initiate a meter testing program in 2016. It is recommended to guide meter replacement based on accuracy testing. | Cleveland, City of Worksheet 2015.xlsx.xls | 5
Cobb County Water System (Cobb County - Marietta Water Authority) | GA0670003 | COBB | 533000 | 31599.84 | 0 | 10145.6 | 21378.4802 | 19287.8 | Note 1 | Note 1 | 14.945 | 19302.745 | 2075.7352 | 228.4251 | 1847.3101 | 2090.6802 | 3461.5 | 181254 | 110 | 141553164.2 | 5.1 | 1947.79 | 1843.4798 | 1164968.12 | 3598172.05 | VPC | 9.779% | 3.385% | 3.4527 | 27.9228 | N/A | 1847.3101 | 1.0021 | 72.5067 | Volume from own sources | Variable production cost (applied to Real Losses) | Unauthorized consumption | 6 | 4 | n/a |  | 9 | 5 | 9 | n/a | n/a | 7 | 5 | 8 | 5 | 9 | 8 | 10 | 7 | 10 | 8 | 5 | QWLA - The combined audit for CCMWA and CCWS is a more accurate way to look at the systems. The low ILI is consistent for the systems. CCWS has a proactive meter replacement program, leak detection program, and large meter testing program. CCWS also has a field verification project through their revenue enhancement program and proactive water line repair and replacement. CCMWA has a proactive capital program with a focus on updating older water mains. The combined systems have a high pressure and the embedded calculation for UARL weighs pressure heavily. | Cobb Co & CCMWA 2015 Water Audit.xls | 5
Cochran Water Department | GA0230000 | BLECKLEY | 5244 | 269.468 | 0 | 0 | 237.7939 | 160.5888 | 0.0125 | 4.742 | 2.9724 | 168.3158 | 69.4781 | 3.5137 | 65.9644 | 77.1925 | 64 | 2716 | 53 | 236413.82 | 3.64 | 388.08 | 14.5792 | 12789.81 | 25599.47 | VPC | 32.46% | 17.5% | 3.5444 | 66.5407 | N/A | 65.9644 | 4.5246 | 62.1079 | Volume from own sources | Billed metered | Customer metering inaccuracies | 5 | 2 | n/a |  | n/a |  | 5 | 10 | 9 | 5 | 5 | 5 | 5 | 10 | 10 | 10 | 1 | 10 | 6 | 4 | QWLA: Tal Woodall -- All inputs have been verified with Water Tech #1, Richard Boyd. Based on observservations made during the validation process, the source meter accuracy test results are in questions. The meters are known dated and, therefore, are unlikely to be significantly over registering. All perofrmance indicators reported within the expected ranges however this may not be an accurate representation of the system. It is recommeneded to have all source meters retested and calibrarted or replaced as needed. It is also recommended to initiate a residential meter testing program. | Cochran, City of Worksheet 2015.xls | 5
College Park | GA1210002 | FULTON | 20382 | 33.193 | 1129.611 | 0 | 1168.5489 | 896.24 | 0 | 12.213 | 14.6069 | 923.0599 | 245.489 | 18.9963 | 226.4928 | 272.3089 | 95 | 3419 | 68 | 5718251 | 1.08 | 4768 | 25.4852 | 20515.98 | 1079917.47 | VPC | 23.3% | 21.48% | 15.2222 | 181.494 | N/A | 226.4928 | 8.8872 | 47.6654 | Water imported | Unbilled metered | Customer metering inaccuracies | 8 |  | 8 |  |  |  | 7 | 7 | 7 | 5 | 5 | 8 | 5 | 8 | 7 | 10 | 8 | 8 | 8 | 7 |  | College Park, City of Worksheet 2015.xls | 5 |  | The utility has not submitted the Water Audit Certification.
Columbia County Water Utility | GA0730000 | COLUMBIA | 101967 | 6147.62 | 0 | 473.417 | 5678.4904 | 4938.951 | Note 1 | 91.19 | 70.9811 | 5101.1221 | 577.3683 | 27.0466 | 550.3217 | 739.5394 | 758 | 44205 | 47.63 | 11273873.79 | 3.64 | 305.91 | 186.5671 | 98449.64 | 168348.9 | VPC | 13.02% | 2.807% | 1.6763 | 34.1077 | N/A | 550.3217 | 2.9497 | 69.736 | Volume from own sources | Variable production cost (applied to Real Losses) | Unauthorized consumption | 7 | 3 | n/a |  | 7 | 3 | 8 | n/a | 6 | 5 | 5 | 7 | 5 | 8 | 8 | 10 | 4 | 8 | 8 | 5 |  | Columbia County 2015 Water Audit.xls | 5
Columbus Water Works | GA2150000 | MUSCOGEE | 229000 | 11994.835 | 5.088 | 732.631 | 11228.5768 | 8636.346 | 0 | 572.763 | 140.3572 | 9349.4662 | 1879.1106 | 277.0827 | 1602.028 | 2592.2308 | 1202 | 76653 | 91.94 | 16462113.37 | 1.68 | 253.29 | 604.0716 | 622281.49 | 405777.66 | VPC | 23.09% | 7.342% | 9.9035 | 57.2596 | N/A | 1602.028 | 2.652 | 84.8128 | Volume from own sources | Unauthorized consumption | Systematic data handling errors | 6 | 5 | n/a |  | 8 | 5 | 10 | n/a | 10 | 5 | 5 | 10 | 9 | 9 | 8 | 10 | 6 | 10 | 9 | 9 | Water Auditor: Jason Jay, QWLA #0084. Contact Info: 706-494-5221; jjay@cwwga.org The Columbus Water Works Water Audit group compiles all data sources into a complementary single workbook titled "WaterAudit_CWW_2015-Data" that contains all the data for all audit items for annual water audit purposes. This spreadsheet provides details as to the data and the sources for each component of the water audit. In addition, all files are stored electonically and organized by audit section. QWLA: Joey Murphy, QWLA #0068. Contact Info: 706-649-3432; jmurphy@cwwga.org[CRUC converted: $/100 cubic feet (ccf) to $/1000 gallons (US)] | Columbus 2015 Water Audit.xls | 5
Commerce | GA1570001 | JACKSON | 6819 | 546.37 | 0 | 130.654 | 415.2176 | 307.039 | 0 | 0 | 5.1902 | 312.2292 | 102.9884 | 6.4814 | 96.507 | 108.1786 | 125.8 | 3958 | 60 | 2647376 | 6.28 | 385.58 | 27.9067 | 40702.96 | 37211.18 | VPC | 26.05% | 3.019% | 4.4864 | N/A | 2101.7714 | 96.507 | 3.4582 | 63.9729 | Volume from own sources | Customer metering inaccuracies | Variable production cost (applied to Real Losses) | 7 | 3 | n/a |  | 5 | n/a | 7 | n/a | n/a | 5 | 5 | 5 | 5 | 9 | 6 | 10 | 6 | 7 | 6 | 5 |  | Commerce 2015 Water Audit.xls | 5
Coosa Water Authority | GA2910006 | UNION | 3944 | 105.23 | 0 | 0 | 105.23 | 72.148 | Note 1 | 0.486 | 1.3154 | 73.9494 | 31.2806 | 0.44344 | 30.8372 | 33.082 | 155 | 3157 | 146 | 713749 | 4.36 | 882.71 | 69.9218 | 1933.42 | 27220.29 | VPC | 31.44% | 4.307% | 0.38483 | N/A | 545.0673 | 30.8372 | 0.44102 | 46.1863 | Volume from own sources | Billed metered | Unbilled metered | 3 |  | n/a |  | n/a |  | 5 | n/a | 5 | 5 | 5 | 5 | 5 | 7 | 2 | 10 | 2 | 9 | 5 | 5 | QWLA Tina Palmer 0096 | Coosa Water Auth Worksheet 2015.xls | 5
Cordele | GA0810001 | CRISP | 10691 | 637.387 | 0 | 0 | 675.516 | 489.63 | 0 | 0 | 8.4439 | 498.0739 | 177.442 | 5.3239 | 172.1182 | 185.886 | 135.1 | 6878 | 64.2 | 1352051 | 3.03 | 208.52 | 41.3028 | 16131.31 | 35890.08 | VPC | 27.52% | 3.978% | 2.1207 | 68.5601 | N/A | 172.1182 | 4.1672 | 68.074 | Volume from own sources | Unauthorized consumption | Systematic data handling errors | 6 | 2 | n/a |  | n/a |  | 7 | 10 | 10 | 5 | 5 | 6 | 5 | 8 | 6 | 10 | 5 | 9 | 8 | 8 | Preparer and reviewer is Debbie Wright, Director of Utilities with the City of Cordele. Water Loss Auditor #0028. Other information gathered from the Finance Dept., Meter Control Dept. and Public Works. Our score was 67 out of 100 and an ILI of 2.56 | Cordele Water Audit 2015.xls | 5
Cornelia | GA1370003 | HABERSHAM | 6130 | 850.47 | 0 | 4.1461 | 854.9145 | 743.094 | 0 | 5.364 | 10.6864 | 759.1444 | 95.7701 | 28.4181 | 67.352 | 111.8205 | 66.1 | 2491 | 97.9 | 2960636 | 9.11 | 421 | 26.1302 | 258860.13 | 28355.19 | VPC | 13.08% | 9.929% | 31.2556 | 74.0771 | N/A | 67.352 | 2.5776 | 67.3883 | Customer metering inaccuracies | Billed metered | Variable production cost (applied to Real Losses) | 8 | 3 | n/a |  | 3 | 2 | 7 | n/a | 5 | 5 | 5 | 5 | 5 | 5 | 6 | 10 | 4 | 8 | 6 | 5 | Nancy Smith (Water Plant Supervisor) prepared the audit. Support people Seth Glaze (Water Sewer Supervisor), Jeremy Mcentire (Meter Tech), Keith Ethridge (Utilities Director) | Cornelia 2015 Water Audit.xls | 5
Covington Water/Sewer Department | GA2170001 | NEWTON | 20379 | 0 | 2198.088 | 971.059 | 1220.6053 | 922.125 | 0 | 0 | 15.2576 | 937.3826 | 283.2227 | 24.1757 | 259.047 | 298.4803 | 160 | 8134 | 80 | 5481066 | 5.56 | 2160 | 60.9024 | 134416.91 | 559541.6 | VPC | 24.45% | 13.26% | 8.143 | 87.2532 | N/A | 259.047 | 4.2535 | 72.2333 | Water imported | Customer retail unit cost (applied to Apparent Losses) | Customer metering inaccuracies | n/a | n/a | 9 | 3 | 9 | n/a | 6 | n/a | n/a | 5 | 5 | 6 | 5 | 6 | 7 | 10 | 8 | 10 | 5 | 10 |  | Covington, City of Worksheet 2015.xls | 5
Coweta County Water & Sewerage Authority | GA0770042 | COWETA | 68803 | 413.146 | 2209.265 | 267.538 | 2431.2976 | 2330.245 | 0 | 10.268 | 30.3912 | 2370.9042 | 60.3934 | 17.7698 | 42.6236 | 101.0526 | 1033.2 | 26642 | 115.1 | 27386952.44 | 7.76 | 3103.67 | 402.7185 | 137893.68 | 330759.1 | CRUC | 4.156% | 2.863% | 1.8274 | N/A | 113.0246 | 42.6236 | 0.10584 | 78.7019 | Water imported | Unauthorized consumption | Systematic data handling errors | 5 | 4 | 5 | 4 | 8 | 3 | 8 | n/a | 7 | 5 | 5 | 8 | 5 | 8 | 7 | 10 | 2 | 9 | 9 | 10 | Coweta County Water & Sewerage Authority's metrics (data and grades) are different from last year due to changes in personnel, reporting and rigerously following the grading matrix. Our apparent losses are 1.55 gallons/connection/day versus 4.35 last year. Both are well within the QWLA guidelines however. This years customer retail cost is $7.91 versus $8.69 last year, which is not significant and certainly within the guidelines. Real losses this year are 40.669 MG/Year versus 118.466 from last year. This reduction is due to our continuing effort to minimize leaks and breaks in our service lines and meters. This years customer retail cost is $3,463.08/million gallons versus $3.78 last year due to the previous employee thinking this was in thousands. This years metric is above guidelines due to our contractual obligations to purchase at a higher cost versus produce the majority of our water. Infrastructure Leakage Index (ILI) is well outside of the guidelines for both periods - possibly due to high pressure in certain zones within our system. | Coweta 2015 Water Audit.xls | 5
Cumming | GA1170000 | FORSYTH | 47541 | 2877.59 | 9.574 | 405.872 | 2481.292 | 2170.593 | 0 | 35.624 | 6.2032 | 2212.4202 | 268.8718 | 28.5883 | 240.2835 | 310.699 | 385 | 19523 | 122.3 | 6702650 | 4.31 | 451.76 | 223.7019 | 123215.36 | 108550.48 | VPC | 12.52% | 3.74% | 4.0119 | 33.7198 | N/A | 240.2835 | 1.0741 | 67.7349 | Volume from own sources | Customer metering inaccuracies | Variable production cost (applied to Real Losses) | 6 | 5 | 8 | 7 | 8 | 7 | 9 | n/a | 8 | 5 | 5 | 9 | 9 | 7 | 8 | 10 | 2 | 10 | 5 | 5 | The City of Cumming’s water system is primarily a new system that consists mainly of ductile iron pipe. Growth has been rapid over the past 20 years and many of the water mains have been replaced through road widening projects. Leak Detection efforts: The City purchased a leak correlator in 2015. The device was used during 2015 to help a subdivision with an 8-inch Master Meter, locate multiple leaks in their system. The resultant leak repairs cut the subdivision’s water usage by 50%. The City is hiring staff in 2016 and plan establish a proactive Leak Detection program. Also in 2015, the City placed a meter on the water main at the Cumming Fairgrounds. This was the last remaining unmetered connection in our system. The correlator was used to discover several leaks at the Fairgrounds. Low ILI is indicative of a hidden data error. Likely suspect is the Volume from own sources incorrect meter error adjustment or in the Authorized Consumption volumes. Recommend a level 2 validation (SCADA and billing record extraction) to validate databases, and level 3 validation (hydraulic field testing) on supply meters to confirm these issues before the next audit. | Cumming, City of Worksheet 2015.xls | 5
Cusseta and Chattahoochee County (Unified Government) | GA0520002 | CHATTAHOOCHEE | 4168 | 118.352 | 0 | 0 | 118.352 | 66.91 | 4.331 | 14.148 | 1.4794 | 86.8684 | 31.4836 | 2.1174 | 29.3662 | 47.111 | 61 | 1534 | 65 | 517067 | 28.1 | 10 | 13.2886 | 59498.94 | 825190.22 | CRUC | 39.81% | 256% | 3.7817 | N/A | 1318.94 | 29.3662 | 2.2099 | 72.1667 | Volume from own sources | Customer metering inaccuracies | Unauthorized consumption | 7 | 5 | n/a |  | n/a |  | 8 | 8 | 8 | 5 | 5 | 5 | 5 | 7 | 8 | 10 | 6 | 5 | 6 | 6 |  | Chattahoochee County Worksheet 2015 - (edited version).xls | 5
Cuthbert | GA2430000 | RANDOLPH | 3500 | 232.361 | 0 | 0 | 232.361 | 113.667 | 0 | 0 | 2.9045 | 116.5715 | 115.7895 | 12.1069 | 103.6826 | 118.694 | 50 | 1270 | 56 | 352505 | 3.9 | 383.67 | Note 3 | 47216.76 | 39779.91 | VPC | 51.08% | 25% | 26.1177 | N/A | 5681.2398 | 103.6826 | Note 3 | 37.3667 | Volume from own sources | Billed metered | Customer metering inaccuracies | 3 | 2 | n/a |  | n/a |  | 2 | n/a | n/a | 5 | 5 | 1 | 5 | 1 | 3 | 10 | 3 | 9 | 4 | 4 | QWLA: Tal Woodall - All information was reviewed and verified with Water Operator, John Hatcher, and City Clerk, Dianne Whatley. Based on the information provided the audit software was unable to calculate the ILI. Based on the size of the system it is believed the length of mains may be exagerated causing the error in this calculation. The city was advised on techniques to more accurately represent the length of mains. The real losses per length of main per day are also extremely exagerated due to missing data from a billed metered account. The city was advised to record all billed metered consumption and to include the data in future audits. The city was also encouraged to initiate production meter testing, customer meter testing, and a meter replacement program, as well as, install meters on those few unmetered connections. | Cuthbert, City of Worksheet 2015.xls | 5
Dade County Water & Sewer Authority | GA0830000 | DADE | 18200 | 747.75 | 0 | 0 | 739.9802 | 496.788 | 0 | 0 | 9.2498 | 506.0378 | 233.9425 | 29.2387 | 204.7038 | 243.1922 | 347 | 8394 | 104 | 3049969 | 4.77 | 536.94 | 119.0566 | 139468.4 | 109913.66 | VPC | 32.86% | 8.339% | 9.5432 | N/A | 1616.2315 | 204.7038 | 1.7194 | 76.1364 | Volume from own sources | Billed metered | Unauthorized consumption | 8 | 9 | n/a |  | n/a |  | 7 | n/a | n/a | 7 | 6 | 7 | 5 | 5 | 5 | 10 | 8 | 10 | 9 | 8 | QWLA: SHERRI L WALKER #0111 Dade County Water Authority is a surface water plant. Source water comes from Lookout Creek and 1 well site that is used for emergency purposes only. | Dade 2015 Water Audit.xls | 5
Dahlonega / Dahlonega Water System | GA1870000 | LUMPKIN | 6214 | 365.455 | 0 | 10.976 | 350.1455 | 256.031 | 0 | 0 | 4.3768 | 260.4078 | 89.7377 | 14.9908 | 74.747 | 94.1145 | 60.5 | 2328 | 150 | 2229314 | 9.83 | 613.18 | 37.0386 | 147359.14 | 45833.34 | VPC | 26.88% | 8.786% | 17.642 | 87.9666 | N/A | 74.747 | 2.0181 | 70.3185 | Billed metered | Customer retail unit cost (applied to Apparent Losses) | Variable production cost (applied to Real Losses) | 9 | 7 |  |  | 5 | 3 | 4 |  |  | 5 | 5 | 4 | 5 | 6 | 6 | 10 | 5 | 8 | 6 | 5 | QWLA John A. Jarrard, #0132, 706-864-3591, dahlonegawater@windstream.net Validity Score of 66 ILI of 2.20 | Dahlonega 2015 Water Audit.xls | 5
Dallas | GA2230000 | PAULDING | 7556 | 0.349 | 206.472 | 0 | 205.733 | 166.667 | 0 | 1.756 | 2.5717 | 170.9947 | 34.7383 | 5.6046 | 29.1337 | 39.066 | 38 | 4008 | 89 | 1651703.41 | 10.23 | 4170 | 26.2082 | 57335.14 | 121487.62 | VPC | 18.99% | 11.92% | 3.8311 | 19.9148 | N/A | 29.1337 | 1.1116 | 76.6812 | Water imported | Variable production cost (applied to Real Losses) | Unauthorized consumption | 5 | 5 | 7 | 3 | n/a | n/a | 10 | n/a | 10 | 5 | 5 | 7 | 5 | 5 | 8 | 10 | 3 | 10 | 10 | 5 | QWLA- Amber Whisner #097 | Dallas 2015 WATER AUDIT.xls | 5
Dalton Utilities | GA3130000 | WHITFIELD | 99315 | 9534.76 | 437.831 | 204.742 | 9767.849 | 6909.42 | Note 1 | Note 1 | 122.0981 | 7031.5181 | 2736.3309 | 255.3866 | 2480.9443 | 2858.429 | 1256.72 | 37100 | 99 | 19142209 | 3.02 | 267.06 | 446.7679 | 771267.46 | 662560.99 | VPC | 29.26% | 7.661% | 18.8595 | N/A | 5408.6095 | 2480.9443 | 5.5531 | 71.8728 | Volume from own sources | Customer metering inaccuracies | Unauthorized consumption | 7 |  | 7 |  | 3 |  | 9 | n/a | n/a | 5 | 5 | 4 | 5 | 10 | 7 | 10 | 8 | 10 | 9 | 7 | Audit was prepared by Seth Lassiter and Validated by QWLA Jonathan Melton. | Dalton 2015 Water Audit.xls | 5
Dawson | GA2730001 | TERRELL | 4836 | 457.766 | 0 | 0 | 457.766 | 236.456 | 0 | 0 | 5.7221 | 242.1781 | 215.5879 | 25.1213 | 190.4666 | 221.31 | 50 | 2535 | 55 | 1055556 | 3.64 | 487.79 | 13.0638 | 91441.58 | 92907.71 | VPC | 48.35% | 17.73% | 27.1501 | 205.8487 | N/A | 190.4666 | 14.5797 | 36.0667 | Volume from own sources | Billed metered | Customer metering inaccuracies | 3 | 2 | n/a |  | n/a |  | 3 | n/a | n/a | 5 | 5 | 1 | 5 | 1 | 5 | 10 | 2 | 5 | 5 | 4 | Please note that the City of Dawson is a poverty stricken town in Southwest Georgia. QWLA: Tal Woodall -- All information for this Audit was provided and verified by water operations specialist Jon Bergozza. The Apparent and Real Losses both reported high and are the result of no meter testing or replacement programs and dated billing and account management software. The ILI also reported high as a result a very high CARL volume likely due to dated supply and customer meters. The utility has had difficulty testing supply meters due the design of pumping facilities. It is recomended to replace any malfunctioning supply meters, initiate a customer meter testing and replacement program, and review account management software update as needed. | Dawson, City of Worksheet 2015.xls | 5
DeKalb County Department of Watershed Management | GA0890001 | DEKALB | 670000 | 22813.42 | 0 | 24.872 | 24251.441 | 22997.46 | Note 1 | Note 1 | 303.143 | 23300.603 | 950.838 | 587.4582 | 363.3798 | 1253.981 | 3030.28 | 191818 | 95 | 73900948 | 2.52 | 200.13 | 1566.1489 | 1480394.59 | 72723.2 | VPC | 5.171% | 2.184% | 8.3906 | 5.1901 | N/A | 363.3798 | 0.23202 | 50.1626 | Volume from own sources | Billed metered | Customer metering inaccuracies | 3 | 9 | n/a | 8 | n/a | 3 | 9 | n/a | 10 | 5 | 5 | 9 | 5 | 9 | 8 | 10 | 8 | 8 | 8 | 5 | QWLA - Amanda Lester (R2T, Inc.) Several data input documents were provided. Meter calibration was not conducted so no calibration reports were provided. Rates are tiered structure based on usage. Billing data was provided by customer type and meter size for all of 2015. | DeKalb Count Worksheet 2015.xls | 5
Demorest | GA1370004 | HABERSHAM | 15130 | 124.82 | 553.75 | 0 | 678.57 | 475.653 | 0 | 1.4656 | 8.4821 | 485.6007 | 192.9693 | 8.925 | 184.0442 | 202.917 | 301 | 6545 | 110 | 2681048 | 7.38 | 1796.11 | 104.7979 | 65866.75 | 330563.7 | VPC | 29.9% | 15.45% | 3.736 | N/A | 1675.1854 | 184.0442 | 1.7562 | 50.0621 | Water imported | Billed metered | Customer metering inaccuracies | 3 | 2 | 4 | 1 | n/a |  | 4 | n/a | 1 | 5 | 5 | 2 | 5 | 3 | 3 | 10 | 2 | 10 | 9 | 10 | QWLA #0071: Spencer Senerman. Bryan Popham is public works director for the City of Demorest. Jill Balenger is a clerk that works for the City of Demorest. Scott Barnhart is the public works director for the City of Baldwin. Lynn Crunkleton is a office manager with the utilities Division for the City of Toccoa. Joely Mixon is a CPA with Mixon and Assiociates. The QWLA advises the City to check inputs for calculation errors next year. Additionally, for future audits, please verify unbilled metered volumes are excluded from billed metered volumes. Finally, ILI appears low because of low connection density, recommend using real losses in gallons/mile/day and apparent losses in gallons/connection/day to assess water system performance. | Demorest, City of Worksheet 2015.xls | 5
Douglas | GA0690002 | COFFEE | 11872 | 1180.4 | 0 | 0 | 1192.3232 | 1002.051 | 0 | 0 | 14.904 | 1016.955 | 175.3682 | 58.2255 | 117.1427 | 190.2722 | 122 | 6364 | 70 | 2613373 | 3.51 | 198.23 | 41.2535 | 204371.37 | 23221.2 | VPC | 15.96% | 8.822% | 25.0663 | 50.4304 | N/A | 117.1427 | 2.8396 | 75.4921 | Variable production cost (applied to Real Losses) | Billed metered | Customer metering inaccuracies | 9 | 3 | n/a |  | n/a |  | 7 | 9 | 4.36 | 1 | 5 | 3 | 5 | 4 | 7 | 10 | 2 | 10 | 8 | 5 | Robert Akins QWLA# 0048 rlakins@esginc.net Met with Kevin Davis Director of Water/Sewer Dept. | Douglas Water Audit 2015.xls | 5
Douglasville - Douglas County Water and Sewer Authority | GA0970000 | DOUGLAS | 110219 | 4077.57 | 141.327 | 1.639 | 4059.222 | 3498.735 | 0 | 0 | 50.7403 | 3549.4753 | 509.7467 | 96.5015 | 413.2452 | 560.487 | 941.9 | 43067 | 98 | 15255682 | 5.43 | 482.16 | 413.3484 | 524003.17 | 199250.32 | VPC | 13.81% | 4.901% | 6.139 | 26.2888 | N/A | 413.2452 | 0.99975 | 78.2573 | Billed metered | Volume from own sources | Unauthorized consumption | 9 | 3 | n/a | n/a | n/a | n/a | 7 | n/a | n/a | 5 | 5 | 7 | 5 | 9 | 9 | 10 | 8 | 9 | 8 | 7 | QWLA #0090 (Daniel Manny) QWLA #0098 (Mike Henry) | Douglasville-Douglas 201 Water Audit.xls | 5
Dublin | GA1750002 | LAURENS | 17500 | 1096.45 | 0 | 0 | 1096.45 | 750.729 | Note 1 | 10.17 | 13.7056 | 774.6046 | 321.8454 | 24.1282 | 297.7172 | 345.721 | 230.2 | 7282 | 62 | 3077496 | 5.22 | 341.49 | 52.9017 | 125900.83 | 101667.15 | VPC | 31.53% | 7.66% | 9.0778 | N/A | 3543.2822 | 297.7172 | 5.6277 | 63.3137 | Volume from own sources | Customer metering inaccuracies | Unbilled metered | 6 | 3 | n/a |  | n/a |  | 7 | n/a | n/a | 5 | 5 | 4 | 5 | 9 | 5 | 10 | 3 | 10 | 10 | 5 | QWLA: Tal Woodall -- All audit data was provided an verified with Utilities Director Michael Clay. All critical performance indicators are within their expected ranges. The Real Losses and ILI are both in the middle range. The Apparent Losses reported on the low end of the range. This is expected to improve with meter upgrades. It is recommended to increase meter accuracy testing to guide replacement. | Dublin, City of Worksheet 2015.xls | 5
East Point Water Treatment plant | GA1210003 | FULTON | 33712 | 2097.97 | 0 | 220.443 | 1799.7496 | 200.767 | 0 | 0 | 22.4969 | 223.2639 | 1576.4857 | 5.0013 | 1571.4844 | 1598.9826 | 175.9 | 12683 | 80 | 2782910 | 3.26 | 500 | 83.3388 | 16304.21 | 785742.21 | VPC | 88.84% | 29.22% | 1.0804 | 339.4652 | N/A | 1571.4844 | 18.8566 | 65.4841 | Volume from own sources | Customer metering inaccuracies | Customer retail unit cost (applied to Apparent Losses) | 8 | 5 |  |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 8 | 7 | 8 | 2 | 8 | 5 | 3 |  | East Point, City of Worksheet 2015.xls | 5
Eastman | GA0910002 | DODGE | 7491 | 379.395 | 0 | 0 | 435.7857 | 285.623 | Note 1 | 7.049 | 5.4473 | 298.1193 | 137.6663 | 45.7035 | 91.9628 | 150.1627 | 64.76 | 3392 | 59 | 2022630 | 1.33 | 288.67 | 18.5018 | 60785.68 | 26546.91 | VPC | 34.46% | 4.496% | 36.9148 | 74.2786 | N/A | 91.9628 | 4.9705 | 49.099 | Volume from own sources | Billed metered | Customer metering inaccuracies | 3 | 2 |  |  |  |  | 6 |  | 9 | 5 | 5 | 5 | 5 | 5 | 5 | 10 | 2 | 10 | 6 | 10 | Audit is prepared by April Sheffield. QWLA is April Sheffield | Eastman 2015 Water Audit.xls | 5
Eatonton Putnam Water & Sewer Authority | GA2370000 | PUTNAM | 12561 | 0 | 353.507 | 0 | 355.3548 | 229.88 | Note 1 | 41.577 | 4.4419 | 275.8989 | 79.4559 | 7.5695 | 71.8864 | 125.4748 | 230 | 8475 | 65 | 2430951 | 9.83 | 2790.01 | 59.6814 | 74408.01 | 200563.85 | VPC | 35.31% | 16.59% | 2.447 | 23.2388 | N/A | 71.8864 | 1.2045 | 74.2511 | Customer metering inaccuracies | Customer retail unit cost (applied to Apparent Losses) | Variable production cost (applied to Real Losses) | n/a |  | 9 | 5 | n/a |  | 7 | n/a | 9 | 5 | 5 | 5 | 5 | 4 | 7 | 10 | 3 | 10 | 5 | 5 | EPWSA is a purchase water system with one connection from the Sinclair Water Authority. QWLA: Tal Woodall -- All data for the audit was provided and verified by EPWSA Director, Donna Van Haute. All of the critical performance indicators reported low within their ranges. These results can be supported by the loss control techniques in place. Some concern was expressed for the position of the flow meter within the Sinclair Water Authority treatment plant. Although the meter has tested accurate with a small degree of error, the flow dynamic within the main is suspected to be causing an unknown degree of error. This may be resulting in skewed performance indicator values. It is recommended to monitor flow data for significant errors. | Eatonton Putnam Water Worksheet 2015.xls | 5
Effingham County Surface Water System | GA1030131 | EFFINGHAM | 9869 | 0 | 754.9559 | 0.17028 | 751.0295 | 602.3285 | Note 1 | 133.764 | 0.01 | 736.1025 | 14.927 | 6.0429 | 8.8841 | 148.701 | 66.75 | 3445 | 45 | 2401687 | 1.68 | 850 | 14.419 | 10152.08 | 14925.33 | CRUC | 19.8% | 10.4% | 4.8058 | 7.0653 | N/A | 8.8841 | 0.61614 | 78.0022 | Total annual cost of operating water system | Water imported | Billed metered | n/a | 1 | 9 | 8 | 9 | 4 | 7 | n/a | 10 | 7 | 5 | 6 | 5 | 8 | 7 | 10 | 3 | 5 | 8 | 10 | The audit was prepared and reviewed by Anthony Allen QWLA #0067. Effingham County Board of Commissioners, 601 N. Laurel Street, Springfield, GA 31329. (912) 754-8060. tallen@effinghamcounty.org. Initial and final screening of the audit metrics showed real losses and ILI as low relative to the average. Our water system is approximatley ten years old so leakge is realtively low. Additionally,the largest portion of flow from the system (Water exported to The City of Rincon, Water sold to a power plant, commercial/industrial users and water flushed for water quality purposes)is metered by meters that are tested anually. Therefore, there is an accurate accounting of water through the system. | Effingham Co 2015 Water Audit.xls | 5
Elberton | GA1050001 | ELBERT | 7800 | 574.452 | 0 | 0 | 578.2104 | 475.231 | 0.252 | 8.363 | 7.2276 | 491.0736 | 87.1367 | 8.755 | 78.3817 | 102.7274 | 122.29 | 3831 | 73 | 1594564 | 4.2 | 493.87 | 32.9396 | 36771.2 | 38710.37 | VPC | 17.77% | 5.217% | 6.2611 | N/A | 1756.0255 | 78.3817 | 2.3796 | 78.6326 | Volume from own sources | Billed metered | Unauthorized consumption | 5 | 3 | n/a | n/a | n/a |  | 3 | 10 | 10 | 5 | 5 | 1 | 5 | 8 | 7 | 10 | 5 | 10 | 8 | 10 | The first of the two finished water meter tests with a -14% error may have been affected by faulty techniques and/or equipment and, therefore, the scores related to supply volume may actually be higher than included herein. By limiting its unbilled, metered water to its own water treatment plant usage and a very small level of billed, un-metered use, the City is demonstrating good control of water use in the distribution system. Potential water losses at its customer meters are likely low due to the City's recent conversion to AMR, but a program of regular testing of accuracy is stil needed. | Elberton Water Audit 2015.xls | 5
Ellijay - Gilmer County Water and Sewerage Authority | GA1230000 | GILMER | 13010 | 996.863 | 0 | 0 | 1011.0172 | 709.005 | Note 1 | 42.855 | 3.7 | 755.56 | 255.4572 | 9.0345 | 246.4227 | 302.0122 | 237 | 5817 | 95 | 2417561 | 4.5 | 445.47 | 74.7149 | 40655.44 | 109773.92 | VPC | 29.87% | 7.08% | 4.2551 | N/A | 2848.6527 | 246.4227 | 3.2982 | 86.3725 | Volume from own sources | Unauthorized consumption | Customer metering inaccuracies | 8 | 8 | n/a |  | n/a |  | 9 | n/a | 10 | 8 | 5 | 8 | 9 | 9 | 9 | 10 | 6 | 10 | 10 | 10 | 2/26/16- WATER UTILITY MEMBERS-GARY MCVEY, DIRECTOR, GARY NIX, WTP SUPER, BONNIE DALRYMPLE, CONTROLLER. Largest customer (poultry plant) initiated a 20% water conservation plan which has reduced total volume of water treated and sold significantly. The Authority has developed a comprehensive plan to seek out areas of large water loss and has identifed specific infrastructures that have failed and is in the process of replacing this infrastructure. It is estimated that their water loss will decrease significantly upon the completiion of this work in March 2016. | Ellijay Gilmer 2015 Water Audit.xls | 5
Etowah Water & Sewer Authority | GA0850007 | DAWSON | 13843 | 532.02 | 4.118 | 14.049 | 516.961 | 423.637 | 0 | 58.019 | 6.462 | 488.118 | 28.843 | 12.1812 | 16.6618 | 93.324 | 187.17 | 5972 | 99 | 3413256 | 9.2 | 342.72 | 68.9597 | 112067.13 | 5710.32 | VPC | 18.05% | 4.098% | 5.5883 | N/A | 243.8888 | 16.6618 | 0.24162 | 75.1667 | Volume from own sources | Billed metered | Customer metering inaccuracies | 8 |  | 7 |  | 7 |  | 10 | n/a | 9 | 5 | 5 | 8 | 5 | 9 | 9 | 10 | 7 | 10 | 10 | 10 |  | Etowah Water & Sewer Auth Worksheet 2015.xls | 5
Fairburn Water Department | GA1210004 | FULTON | 14000 | 0 | 393.404 | 0 | 398.3838 | 330.6 | 0 | 0 | 4.9798 | 335.5798 | 62.804 | 5.1619 | 57.6421 | 67.7838 | 71.1 | 5747 | 75 | 3179991 | 6.36 | 5000 | 34.1284 | 32829.39 | 288210.73 | VPC | 17.01% | 10.88% | 2.4608 | 27.4793 | N/A | 57.6421 | 1.689 | 67.1358 | Water imported | Customer metering inaccuracies | Billed metered | n/a | n/a | 6 | 4 | n/a | n/a | 7 | n/a | n/a | 5 | 5 | 4 | 5 | 8 | 8 | 10 | 6 | 8 | 10 | 10 | QWLA: John Caldwell, Registration # 0101 Units are correct | Fairburn 2015 Water Audit.xls | 5
Fayette County Water System | GA1130001 | FAYETTE | 74163 | 3916.323 | 59.952 | 334.233 | 3646.0905 | 3111.9485 | 2.646 | 1.159 | 45.5761 | 3161.3297 | 484.7608 | 80.4279 | 404.3329 | 531.4959 | 629 | 38812 | 94 | 15846990 | 3.47 | 372.07 | 316.4991 | 279084.83 | 150441.13 | VPC | 14.58% | 2.82% | 5.6774 | 28.5417 | N/A | 404.3329 | 1.2775 | 74.1471 | Volume from own sources | Customer metering inaccuracies | Customer retail unit cost (applied to Apparent Losses) | 7 | 7 | 5 | 1 | 7 | 5 | 7 | 10 | 9 | 5 | 5 | 7 | 5 | 6 | 8 | 10 | 8 | 10 | 6 | 8 | QWLA: Daphne Cousson; QWLA # 0110 | Fayette County 2015 Water Loss Audit.xls | 5
Fayetteville | GA1130003 | FAYETTE | 15281 | 207.22 | 334.233 | 0 | 539.9104 | 483.54 | 0 | 0 | 6.7489 | 490.2889 | 49.6215 | 7.4429 | 42.1787 | 56.3704 | 92 | 7880 | 60 | 2661502 | 3.18 | 1190 | 36.7859 | 23668.32 | 50192.62 | VPC | 10.44% | 3.077% | 2.5877 | 14.6647 | N/A | 42.1787 | 1.1466 | 64.5195 | Volume from own sources | Variable production cost (applied to Real Losses) | Customer metering inaccuracies | 8 | 2 | 5 | 2 | n/a |  | 7 | n/a | n/a | 5 | 5 | 5 | 5 | 8 | 8 | 10 | 4 | 10 | 6 | 4 | QWLA: Tal Woodall -- All data was provided and verified by Chris Hindman, Director of Public Services, and Doug Gonsalves, Operation Manager. All of the performance indicators reported very low. The system does have good loss control practices in place, however, these values may not be entirely accurate due to the unknown accuracy of the import meters. It is recommended to review and updated meter management policies and procedures with the supplier. | Fayetteville, City of Worksheet 2015.xls | 5
Fitzgerald Utilities | GA0170000 | BEN HILL | 12935 | 879.7146 | 0 | 0 | 837.8234 | 458.2449 | Note 1 | 6.157 | 10.4728 | 474.8747 | 362.9487 | 4.4041 | 358.5447 | 379.5785 | 125 | 5825 | 65 | 921603.36 | 2.19 | 154.51 | 36.7737 | 9644.95 | 55398.73 | VPC | 45.31% | 7.336% | 2.0714 | 168.6376 | N/A | 358.5447 | 9.75 | 56.1471 | Volume from own sources | Unbilled metered | Customer metering inaccuracies | 5 | 2 |  |  |  |  | 6 |  | 3 | 5 | 5 | 4 | 5 | 4 | 4 | 10 | 2 | 8 | 8 | 5 |  | Fitzgerald 2015 WaterAudit.xls | 5
Floyd County Water | GA1150001 | FLOYD | 41738 | 1297.552 | 531.161 | 22.568 | 1769.8273 | 1388.424 | 0 | 0 | 22.1228 | 1410.5468 | 359.2805 | 50.8366 | 308.4439 | 381.4033 | 567 | 18216 | 80 | 5118884 | 4.89 | 614.74 | 169.3562 | 248590.86 | 189612.8 | VPC | 21.55% | 8.826% | 7.6459 | 46.3906 | N/A | 308.4439 | 1.8213 | 72.4342 | Volume from own sources | Variable production cost (applied to Real Losses) | Water imported | 8 | 8 | 5 | 8 | 5 | 8 | 8 | n/a | n/a | 8 | 5 | 5 | 5 | 8 | 8 | 10 | 8 | 10 | 7 | 8 |  | Floyd County Water Worksheet 2015.xls | 5
Folkston | GA0490000 | CHARLTON | 5940 | 245.455 | 0 | 1.206 | 246.8965 | 222.984 | 0 | 1.2599 | 1.24 | 225.4839 | 21.4127 | 3.4398 | 17.9729 | 23.9125 | 58.26 | 2269 | 52 | 562036 | 3.58 | 237.64 | 12.4421 | 12314.45 | 4271.07 | VPC | 9.685% | 3.057% | 4.1534 | 21.7015 | N/A | 17.9729 | 1.4445 | 67.4533 | Volume from own sources | Unbilled metered | Customer metering inaccuracies | 8 | 3 |  |  | 8 | 3 | 6 |  | 3 | 8 | 5 | 4 | 5 | 3 | 6 | 10 | 4 | 10 | 9 | 6 | QWLA - Reviewed their audit and supporting documentation had call with staff 6/2/16 to validate data notes below. | Folkston, City of Worksheet 2015-Peter.xls | 5
Forsyth | GA2070001 | MONROE | 7400 | 503.57 | 0 | 8.544 | 495.1633 | 439.11 | Note 1 | Note 1 | 6.1895 | 445.2995 | 49.8638 | 30.364 | 19.4998 | 56.0533 | 50 | 2870 | 75 | 1993908 | 3.86 | 378.42 | 19.1899 | 117204.97 | 7379.11 | VPC | 11.32% | 6.366% | 28.9857 | 18.6147 | N/A | 19.4998 | 1.0162 | 54.8315 | Billed metered | Volume from own sources | Customer metering inaccuracies | 8 | 3 | n/a |  | 5 | 5 | 2 | n/a | n/a | 5 | 5 | 3 | 5 | 1 | 6 | 10 | 3 | 6 | 5 | 2 | Water auditor Qwla # 0046, Bentley Cox, w/ Pat Wright, Project Manager City of Forsyth Water Department SID# GA2070001 2015 audit report. | Forsyth, City of Worksheet 2015.xls | 5
Forsyth County Water and Sewer | GA1170050 | FORSYTH | 138368 | 5159.0577 | 259.5609 | 11.5251 | 5396.7948 | 4904.72 | Note 1 | Note 1 | 67.4599 | 4972.1799 | 424.6149 | 75.2964 | 349.3185 | 492.0748 | 1009.35 | 57931 | 114 | 17037327.16 | 5.94 | 1220 | 588.7912 | 447260.7 | 426168.56 | VPC | 9.118% | 5.61% | 3.561 | 16.5203 | N/A | 349.3185 | 0.59328 | 81.3149 | Billed metered | Variable production cost (applied to Real Losses) | Unauthorized consumption | 9 | 3 | 9 | 3 | 5 | 2 | 7 | n/a | n/a | 5 | 5 | 7 | 5 | 9 | 6 | 10 | 10 | 10 | 9 | 6 | Barry H. Lucas, QWLA Registry #0131, Audit completed on 5-16-2016 | Forsyth County Worksheet 2015-Peter.xls | 5
Fort Oglethorpe | GA0470001 | CATOOSA | 9446 | 0 | 332.6 | 0 | 332.6 | 198 | 0.006 | 0 | 4.1575 | 202.1635 | 130.4365 | 5.3673 | 125.0692 | 134.594 | 38 | 3042 | 105 | 1407175 | 7.57 | 1.58 | 25.3666 | 40630.58 | 946773.72 | CRUC | 40.47% | 72.41% | 4.834 | 112.6415 | N/A | 125.0692 | 4.9305 | 78.4608 | Billed metered | Billed unmetered | Customer metering inaccuracies | n/a | n/a | 10 | n/a | n/a | n/a | 5 | 5 | n/a | 5 | 5 | 5 | 5 | 8 | 5 | 10 | 5 | 10 | 8 | 10 | QWLA: Sherri L Walker #0111 The City of Ft. Oglethorpe is a purchased water system. The system maintains no pumps and treats no water. All water is imported from Tennessee American Water Company. Interviewed: Michael Housley - Plant Manager | Fort Oglethorpe Water Audit 2015.xls | 5
Fort Valley Utility Commission | GA2250001 | PEACH | 16430 | 514.979 | 0 | 0 | 523.7785 | 469.889 | 0.025 | 0 | 6.5472 | 476.4612 | 47.3172 | 17.0168 | 30.3004 | 53.8645 | 152 | 5325 | 55 | 2531882.04 | 5.35 | 438.52 | 32.543 | 91039.98 | 13287.34 | VPC | 10.28% | 4.234% | 8.7552 | 15.5896 | N/A | 30.3004 | 0.93109 | 59.5608 | Volume from own sources | Customer metering inaccuracies | Variable production cost (applied to Real Losses) | 5 | 7 | n/a |  | n/a |  | 7 | 6 | n/a | 5 | 5 | 4 | 5 | 8 | 4 | 10 | 4 | 5 | 6 | 4 | There are 3- treatment facilities that treat water. There are 6 wells that produce our output. There are 6- storage tanks and 2- reservoirs that have 1.85 mg capacity. There is no imported or exported water. We have a scada system at the plants that keep history. Keith Spillers kspillers@fvutil.com QWLA: Tal Woodall -- All inputs, grading, and comments were discussed and verified with Water Superintendent Keith Spillers. The major performence indicators are all on the lower end of each range. This is supported by the age of the infrustructure and the high qualty/ accuracy of system maps. | Fort Valley UCaudit2015verified.xlssentcopy.xls | 5
Gainesville Public Utilities | GA1390001 | HALL | 140000 | 6876.904 | 0 | 0 | 6848.094 | 5882 | Note 1 | Note 1 | 32.111 | 5914.111 | 933.983 | 216.8242 | 717.1588 | 966.094 | 1373 | 54807 | 121 | 27001232 | 5.72 | 254.74 | 691.1372 | 1240234.68 | 182689.02 | VPC | 14.11% | 5.3% | 10.8387 | 35.8498 | N/A | 717.1588 | 1.0377 | 75.4743 | Volume from own sources | Billed metered | Customer metering inaccuracies | 7 | 6 | n/a | 5 | n/a | 5 | 7 | n/a | n/a | 7 | 5 | 6 | 9 | 10 | 10 | 10 | 7 | 10 | 7 | 9 | QWLA: Joey Leverette | Gainesville 2015 Water Audit.xls | 5
Garden City | GA0510000 | CHATHAM | 8141 | 344.18 | 0 | 0 | 332.292 | 251.595 | Note 1 | 22.629 | 4.726 | 278.95 | 53.342 | 7.0561 | 46.2859 | 80.697 | 41 | 3563 | 57 | 1312371.78 | 5.64 | 199.23 | 15.734 | 39796.55 | 9221.53 | VPC | 24.28% | 4.15% | 5.4257 | 35.591 | N/A | 46.2859 | 2.9418 | 60.2859 | Volume from own sources | Customer retail unit cost (applied to Apparent Losses) | Variable production cost (applied to Real Losses) | 5 | 3 | n/a |  | n/a |  | 6 | n/a | 10 | 10 | 5 | 8 | 5 | 10 | 10 | 10 | 3 | 10 | 5 | 5 | Audited by Sally Draeger, QWLA # 0018 | Garden City Water Audit 2015.xls | 5
Glen of Robin Hood / Montgomery Area | GA0510109 | CHATHAM | 5000 | 165.086 | 0 | 0 | 165.086 | 143.726 | 0 | 0 | 2.0636 | 145.7896 | 19.2964 | 9.946 | 9.3504 | 21.36 | 27.7 | 2425 | 45 | 265685 | 1.75 | 256 | 8.436 | 17405.55 | 2393.7 | VPC | 12.94% | 7.651% | 11.2369 | 10.5639 | N/A | 9.3504 | 1.1084 | 66.5333 | Volume from own sources | Customer metering inaccuracies | Billed metered | 4 | 3 | n/a |  | n/a |  | 8 | n/a | 8 | 5 | 5 | 3 | 1 | 5 | 4 | 10 | 3 | 2 | 8 | 2 | [CRUC converted: $/100 cubic feet (ccf) to $/1000 gallons (US)] | Glen of Robinhood Worksheet 2015.xls | 4.2 |  | The utility has not submitted the Water Audit Certification.
Glennville | GA2670002 | TATTNALL | 5173 | 251.794 | 0 | 0 | 250.3122 | 203.645 | 0 | 6.392 | 3.1289 | 213.1659 | 37.1463 | 2.1904 | 34.9559 | 46.6672 | 52 | 2088 | 50 | 887595 | 3.74 | 233.4 | 10.85 | 8191.93 | 8158.71 | VPC | 18.64% | 2.092% | 2.874 | 45.8667 | N/A | 34.9559 | 3.2217 | 71.5921 | Volume from own sources | Total annual cost of operating water system | Billed metered | 8 | 2 | n/a |  | n/a |  | 5 | n/a | 1 | 5 | 5 | 3 | 5 | 2 | 5 | 10 | 1 | 4 | 9 | 10 | QWLA 0071: Spencer Senerman. City Manager of Glennville is Amy Murray. Public Works Director of Glennville is Stan Dansby. Delilah Bryant works in the billing department for the City of Glennville. Bo Lamb is the inspector in charge of the meter replacement project for the City of Glennville. General condition of audit was good. Glennville was prepared for teleconference and all of their data was organized. The City should consider starting an annual customer meter accuracy testing program. The City should test about 1% (20) of its meters to determine the actual percent inaccuracy of its metered population. The apparent losses increased when compared to the 2014 Water Audit due to the increase in customer meter inaccuracy (estimated to be around 7%). Apparent losses will likely decrease in 2016 becase of the City's current meter replacement program. The ILI increased because of a decrease in unavoidable real losses. The unavoidable real losses decreased due to a decrease in the average system pressure, number of active and inactive connections, and length of customer service line. Number of active and inactive service connections changed due to field validation of service connections. | Glennville, City of Worksheet 2015.xls | 5
Gray | GA1690000 | JONES | 8885 | 122.922 | 112.0799 | 9.431 | 232.5473 | 149.4481 | 0 | 7.204 | 2.9068 | 159.5589 | 72.9884 | 5.7999 | 67.1885 | 83.0992 | 70 | 2127 | 50 | 800193.5 | 6.88 | 2042.28 | 12.7339 | 39903.85 | 137217.54 | VPC | 35.73% | 24.72% | 7.4707 | N/A | 2629.6872 | 67.1885 | 5.2763 | 56.2519 | Water imported | Unbilled metered | Customer metering inaccuracies | 8 | 3 | 5 | 3 | 5 | 3 | 3 | n/a | 4 | 5 | 5 | 1 | 5 | 4 | 7 | 10 | 2 | 5 | 6 | 5 | QWLA: TAL WOODALL -- THIS AUDIT WAS REVIEWED AND VERIFIED WITH WATER PLANT OPERATOR, CHEYENNE MORGAN. ALL PERFORMANCE INDICATORS REPORTED IN THEIR EXPECTED RANGES. ILI AND REAL LOSSES WERE IN THE MID RANGE AND APPARENT LOSSES WERE IN THE MID TO LOW RANGE. THESE IS SUPPORTED BY THE CURRENT WATER LOSS CONTROL PRACTICES. THESE NUMBERS ARE EXPECTED TO IM PROVE WITH THE PLANNED CUSTOMER METER UPGRADE. IT IS RECOMMENDED TO BEGIN A CUSTOMER METER TEESTING PROGRAM AND INCLUDE UNBILLED METERS IN MONTHLY READINGS. | Gray, City of the Worksheet 2015.xls | 5
Greensboro Water Department | GA1330000 | GREENE | 3156 | 244.549 | 0 | 0 | 244.549 | 172.474 | 0 | 0 | 3.0569 | 175.5309 | 69.0181 | 6.3768 | 62.6413 | 72.075 | 41.4 | 1746 | 75 | 1119467.99 | 8.47 | 576.57 | 13.3008 | 54011.54 | 36117.11 | VPC | 29.47% | 8.208% | 10.0061 | 98.2933 | N/A | 62.6413 | 4.7096 | 65.5222 | Volume from own sources | Customer metering inaccuracies | Variable production cost (applied to Real Losses) | 7 |  | n/a |  | n/a |  | 7 | 9 | 5 | 5 | 5 | 5 | 5 | 7 | 7 | 10 | 3 | 10 | 6 | 5 | Auditor: Richard R. Pendergrass, License # 0126, Cell 770-402-0377, Email: rpendergrass@pnaeng.com | Greensboro 2015 Water Audit.xls | 5
Griffin | GA2550000 | SPALDING | 23643 | 3318.89 | 0 | 1981.9926 | 1336.8974 | 727.0955 | 0 | 39.542 | 16.7112 | 783.3487 | 553.5487 | 16.8347 | 536.714 | 609.8019 | 212.8 | 11331 | 73 | 5359925 | 6.69 | 353.6 | 75.9622 | 112623.91 | 189782.08 | VPC | 45.61% | 6.013% | 4.0705 | 129.7722 | N/A | 536.714 | 7.0655 | 77.2988 | Volume from own sources | Variable production cost (applied to Real Losses) | Water exported | 7 | 5 | n/a |  | 8 | 5 | 10 | n/a | 9 | 5 | 5 | 9 | 5 | 10 | 9 | 10 | 6 | 10 | 9 | 5 |  | Griffin, City of Worksheet 2015.xls | 5
Grovetown Water System | GA0730001 | COLUMBIA | 12165 | 12.5 | 333.394 | 0 | 346.9643 | 290.2674 | 0 | 0 | 4.3371 | 294.6045 | 52.3598 | 9.0358 | 43.324 | 56.6969 | 67 | 5063 | 80 | 1590783 | 6.18 | 1845.63 | 32.7601 | 55841.45 | 79960.01 | VPC | 16.34% | 9.04% | 4.8895 | 23.4438 | N/A | 43.324 | 1.3225 | 71.1233 | Customer metering inaccuracies | Customer retail unit cost (applied to Apparent Losses) | Variable production cost (applied to Real Losses)
Gwinnett County Department of Water Resources | GA1350004 | GWINNETT | 795657 | 27098.594 | 0 | 791.82 | 26295.2535 | 23322.223 | 0 | 23.262 | 14.547 | 23360.032 | 2935.2215 | 302.551 | 2632.6705 | 2973.0305 | 3743.89 | 259697 | 110 | 23134521 | 5.43 | 192.39 | 2377.2411 | 1642851.82 | 506499.47 | VPC | 11.31% | 9.322% | 3.1918 | 27.7739 | N/A | 2632.6705 | 1.1074 | 74.4269 | Volume from own sources | Customer metering inaccuracies | Variable production cost (applied to Real Losses) | 7 | 3 | n/a |  | 9 | 3 | 9 | n/a | 10 | 8 | 5 | 7 | 5 | 10 | 10 | 10 | 9 | 10 | 8 | 6 |  | Gwinnett Co 2015 Water Audit FINAL.xls | 5
Hampton | GA1510000 | HENRY | 7305 | 31.847 | 169.085 | 0 | 212.3368 | 146.065 | Note 1 | Note 1 | 2.6542 | 148.7192 | 63.6176 | 1.7777 | 61.8399 | 66.2718 | 40.9 | 2908 | 54 | 947412 | 5.97 | 3162.72 | 12.9587 | 10612.78 | 195582.27 | VPC | 31.21% | 22.65% | 1.6748 | 58.2615 | N/A | 61.8399 | 4.7721 | 60.193 | Water imported | Billed metered | Customer metering inaccuracies | 3 | 3 | 8 | 1 |  |  | 6 |  |  | 5 | 5 | 5 | 5 | 6 | 6 | 10 | 3 | 5 | 6 | 6 | QWLA Comments - Hampton water volume from own sources is three ground water wells (#5, #6, & #7). QWLA recommends that City of Hampton start entering data in AWWA Compiler software to more easily compare prior year water audits. | Hampton, City of Worksheet 2015.xls | 5
Hapeville Water Department | GA1210006 | FULTON | 6500 | 0 | 316 | 0 | 316.1581 | 271 | 0 | 1 | 3.952 | 275.952 | 40.2061 | 7.0189 | 33.1872 | 45.1581 | 24.1 | 2351 | 75 | 3155148 | 9.96 | 4941.93 | 13.223 | 69908.4 | 330544.39 | CRUC | 14.28% | 14.26% | 8.1795 | 38.6745 | N/A | 33.1872 | 2.5098 | 56.4797 | Water imported | Unbilled metered | Customer metering inaccuracies | n/a |  | 7 | 1 | n/a |  | 5 | n/a | 3 | 5 | 5 | 3 | 5 | 4 | 5 | 10 | 3 | 3 | 5 | 10 | QWLA: John Payne, Keck & Wood, Inc. QWLA No. 0122. | Hapeville Water Department Worksheet 2015.xls | 5
Haralson County Water Authority | GA1430007 | HARALSON | 11362 | 746.608 | 85.691 | 477.247 | 345.7142 | 249.118 | 0 | 0.386 | 4.3214 | 253.8254 | 91.8887 | 23.1831 | 68.7057 | 96.5962 | 382.7 | 4912 | 88.4 | 2918067 | 6.21 | 427.1 | 90.5773 | 143966.93 | 29344.19 | VPC | 27.94% | 6.008% | 12.9306 | N/A | 491.8597 | 68.7057 | 0.75853 | 78.0983 | Customer metering inaccuracies | Billed metered | Variable production cost (applied to Real Losses) | 9 | 3 | 10 | 3 | 10 | 3 | 6 | n/a | 10 | 5 | 5 | 3 | 5 | 7 | 8 | 10 | 3 | 10 | 9 | 6 | QWLA: HCWA covers a large Hilly, mostly Rural service area with Mainlines. Pressures vary widely but are controlled by PRV valves. There is a small number of service connections in comparison to the miles of service Mains. The Weighted average pressure is relatively high, for these reasons the ILI number is very low. The Distribution System Team members do actively search for and repair leaks, even though no extensive leak control programs are in place. Much of HCWA water is Exported. | Haralson 2015 Water Audit.xls | 5
Harlem | GA0730002 | COLUMBIA | 5356 | 0 | 173.278 | 0 | 172.4708 | 138.591 | 0.0012 | 6.347 | 2.1559 | 147.0951 | 25.3758 | 5.2603 | 20.1155 | 33.8786 | 63 | 2368 | 70 | 940727 | 7.46 | 2001.56 | 17.7836 | 39241.64 | 40262.34 | VPC | 19.64% | 10.26% | 6.086 | 23.2732 | N/A | 20.1155 | 1.1311 | 64.119 | Water imported | Billed metered | Unbilled metered | n/a | n/a | 7 | 3 | n/a | n/a | 4 | 3 | 4 | 5 | 5 | 4 | 5 | 6 | 5 | 10 | 3 | 10 | 6 | 10 | QWLA: Robert H. Fields Jr. (0058) Point of Contact: Robert H. Fields Jr. 706-556-3500 | Harlem 2015 Water Loss Audit.xls | 5
Harris County Waterworks | GA1450011 | HARRIS | 20062 | 616.2 | 321.3735 | 1.5083 | 978.0652 | 803.8325 | 0 | 0.0505 | 12.2258 | 816.1088 | 161.9564 | 25.0671 | 136.8893 | 174.2327 | 400.7 | 8324 | 92 | 3915400.99 | 5.76 | 1312.25 | 114.7223 | 144471.28 | 179633.4 | VPC | 17.81% | 8.689% | 8.2505 | N/A | 935.9599 | 136.8893 | 1.1932 | 50.073 | Volume from own sources | Water imported | Unbilled metered | 5 | 3 | 3 | 4 | 3 | 4 | 6 | n/a | 3 | 5 | 5 | 3 | 5 | 7 | 6 | 10 | 4 | 10 | 5 | 5 | HCWW Water Loss Auditor: Abby Bridges, ph 706-323-0593, e-mail: harrisplant@bellsouth.net QWLA: David L. Hamby, Certification # 0027, ph 706-323-0593, e-mail: harrisplant@bellsouth.net Water Production from own sources & water imported & water exported are less this year compared to previous years due to cooler weather and more rainfall. Also the SCADA system was repaired in August of 2015 giving better control of water pumping. Some errors were made on the previous year's audits that were corrected on this year's audit. They are noted below in the comments for Unbilled metered & CRUC | Harris Co 2015 Water Audit.xls | 5
Hart County Water and Sewer Authority | GA1470065 | HART | 4059 | 0 | 222.965 | 28 | 195.7313 | 176 | 0 | 0 | 2.4466 | 178.4466 | 17.2846 | 3.2294 | 14.0552 | 19.7313 | 116.8 | 1847 | 106 | 1223625 | 4.92 | 2014.28 | 35.1668 | 15888.64 | 69151.75 | CRUC | 10.08% | 7.934% | 4.7903 | N/A | 329.6874 | 14.0552 | 0.39967 | 45.9447 | Water imported | Customer metering inaccuracies | Total annual cost of operating water system
Hartwell | GA1470000 | HART | 7116 | 460.682 | 0 | 88.8291 | 366.3488 | 271.0145 | 0.0593 | 9.1885 | 6.294 | 286.5563 | 79.7925 | 9.3688 | 70.4237 | 95.275 | 85.115 | 2807 | 78.7789 | 1220855.54 | 3.96 | 413.44 | 25.3475 | 37100.55 | 29116.25 | VPC | 26.01% | 5.948% | 9.1443 | 68.7359 | N/A | 70.4237 | 2.7783 | 64.3686 | Volume from own sources | Variable production cost (applied to Real Losses) | Unbilled metered | 7 | 2 | n/a |  | 7 | 3 | 7 | 10 | 5 | 8 | 5 | 5 | 5 | 2 | 3 | 10 | 3 | 10 | 5 | 4 | Audit Info Spreadsheet For Year - Spreadsheet is an anuual compilation of various monthly parameters of Water pumped into distribution system, Billed Metered obtained from the Utility Billing System, Water Truck Hydrant Meter - Misc. Metered Consumption Billed Outside of Billing System, Water Dept. Hydrant Meter - Billed Outside of Billing System, Billed Unmetered, Unbilled Metered - Water Dept. Hydrant Meter for City Usage, Water Usage at Water Treatment Facility For Chemical Feed System and Domestic Use, Water Dept. Metered Flushing, Unbilled Unmetered - City Fire Dept. Usage Est., County Fire Dept. Flushing, Unmetered Connection Usage, and Water Dept Flushing Losses. System is vigilint in keeping up records month by month building towards yearly data. Various departments throughout the City work together to provide reports for these various parameters. | Hartwell 2015 Water Audit.xls | 5
Hawkinsville | GA2350001 | PULASKI | 4856 | 277.855 | 0 | 0 | 277.8272 | 232.33 | 0 | 4.012 | 3.4728 | 239.8148 | 38.0124 | 6.0987 | 31.9137 | 45.4972 | 60 | 2003 | 55 | 269385.03 | 2.6 | 444.67 | 12.5479 | 15856.62 | 14191.06 | VPC | 16.38% | 12.39% | 8.3419 | 43.6519 | N/A | 31.9137 | 2.5434 | 63.2539 | Volume from own sources | Customer metering inaccuracies | Billed metered | 9 | 3 | n/a |  | n/a |  | 7 | 10 | 10 | 5 | 5 | 5 | 5 | 7 | 6 | 10 | 4 | 10 | 9 | 10 | Brandon Lewis QWLA#0112: Water audit for the City of Hawkinsville for the calendar year of 2015. Primary audit preparer, Lance Woods with Ocmulgee, Inc. City personnel interviewed: Chelsea Tyner (Billing Clerk), Hugh Staple (Collections and Distribution Supervisor), Guy Smith (WTP Manager), and Judy Davis (City Accountant). Overall data validity score reduced from 83 to 81 after audit certification was performed. | Hawkinsville, City of Worksheet 2015.xls | 5
Hazlehurst | GA1610001 | JEFF DAVIS | 5504 | 324.688 | 0 | 0 | 324.688 | 247.85 | 0.80225 | 8.924 | 9.093 | 266.6692 | 58.0188 | 14.2584 | 43.7604 | 76.0358 | 70 | 2511 | 51 | 567092 | 2.67 | 176.1 | 14.0608 | 38069.9 | 7706.2 | VPC | 23.42% | 8.632% | 15.5572 | 47.7465 | N/A | 43.7604 | 3.1122 | 56.6404 | Volume from own sources | Systematic data handling errors | Billed unmetered | 1 | 1 | n/a |  | n/a |  | 10 | 8 | 8 | 5 | 5 | 8 | 5 | 3 | 8 | 10 | 2 | 10 | 8 | 9 | Bill Powell, QWLA Number 0030. Met with Lorrie Williams and Blan Williams. | Hazlehurst, City of Worksheet 2015.xls | 5
Heard County Water Authority | GA1490000 | HEARD | 8172 | 453.8 | 0 | 39.07 | 410.964 | 248.115 | Note 1 | 1.711 | 5.1371 | 254.9631 | 156.001 | 6.7462 | 149.2548 | 162.849 | 400 | 3715 | 80 | 1599762 | 7.13 | 790.12 | 79.4605 | 48100.32 | 117929.21 | VPC | 39.63% | 10.72% | 4.9752 | N/A | 1022.2932 | 149.2548 | 1.8784 | 70.0037 | Customer metering inaccuracies | Customer retail unit cost (applied to Apparent Losses) | Variable production cost (applied to Real Losses) | 9 | 3 | n/a |  | 5 | 3 | 7 | n/a | 9 | 5 | 5 | 3 | 5 | 1 | 7 | 10 | 1 | 10 | 5 | 5 | QWLA: Bryant Snyder cert # 0127 I am also responsible for the preparation and gathering of data needed for HCWA water audit. All notes were recorded by Bryant Snyder. | Heard Co. Water Audit 2015.xls | 5
Henry County Water Authority | GA1510001 | HENRY | 218667 | 6382.3921 | 27.8512 | 400.104 | 5664.6625 | 4881.3438 | 0 | 82.3986 | 10.5206 | 4974.2629 | 690.3996 | 154.2389 | 536.1607 | 783.3187 | 1346.83 | 66811 | 102.5 | 33916569 | 5.9 | 338.96 | 647.5356 | 909714.26 | 181737.03 | VPC | 13.83% | 3.311% | 6.3249 | 21.9864 | N/A | 536.1607 | 0.828 | 84.0394 | Volume from own sources | Unauthorized consumption | Billed metered | 7 | 7 | 3 | 1 | 8 | 1 | 9 | 10 | 9 | 8 | 7 | 9 | 7 | 9 | 9 | 10 | 10 | 10 | 10 | 10 | QWLA: Patrick L. Kelley [678-583-3827]; QWLA Registry Number: 0069 Utility Name: Henry County Water Authority; PWS ID#: GA1510001 Water Loss Audit Year: 2015 Calendar Year General Notes: HCWA has a fairly young system and is extremely active in water loss efforts (leak detection and other), meter accuracy testing (excluding production meters...see volume from own sources), and meter changeout. The ILI score is under 1, but it is likely due to the age of the system and HCWA's proactive approach. Another thing that drastically affects the ILI was the number of service connections. The 66,004 count includes all end points (as directed by water loss experts) and it should be noted the actual taps on the mains are a lot less (there are a number of single taps that are split to serve multiple meters). HCWA has been actively upgrading service lines to copper over the last 5 years. | Henry Co. 2015 Water Audit.xls | 5
Hephzibah | GA2450002 | RICHMOND | 4500 | 190.426 | 0 | 0 | 190.426 | 157.0096 | 0 | 1.25 | 2.3803 | 160.6399 | 29.7861 | 4.9265 | 24.8596 | 33.4164 | 50 | 1762 | 70 | 523658 | 2.71 | 684.77 | 13.6641 | 13350.89 | 17023.1 | VPC | 17.55% | 6.275% | 7.6602 | 38.6541 | N/A | 24.8596 | 1.8193 | 47.7157 | Volume from own sources | Unbilled metered | Customer metering inaccuracies
Hiawassee | GA2810000 | TOWNS | 5496 | 457.37 | 0 | 229.475 | 226.4736 | 161.725 | 0.14 | 0.127 | 2.8309 | 164.8229 | 61.6506 | 1.9475 | 59.7032 | 64.6086 | 75.4 | 2566 | 95 | 1903821 | 7.25 | 900 | 27.4908 | 14119.16 | 53732.85 | VPC | 28.53% | 3.704% | 2.0793 | 63.7453 | N/A | 59.7032 | 2.1717 | 52.1157 | Volume from own sources | Water exported | Unbilled metered | 5 | 3 | n/a |  | 5 | 3 | 5 | 8 | 4 | 5 | 5 | 4 | 5 | 6 | 3 | 10 | 2 | 10 | 5 | 5 | Water audit certificaiton performed by Fletcher Holliday and Chris Hinson. City staff participating in audit preparation: City Administrator, Utility Billing Clerk, Water Plant Superintendent and his assistant. | Hiawassee 2015 Water Audit.xls | 5
Hinesville | GA1790000 | LIBERTY | 24666 | 1047.182 | 0 | 0 | 1036.8139 | 908.5258 | 0.312 | 11.719 | 12.9602 | 933.517 | 103.2969 | 7.1697 | 96.1272 | 127.9761 | 184.398 | 13609 | 42 | 1985834 | 4.58 | 176.6 | 46.587 | 32837.35 | 16976.06 | VPC | 12.34% | 2.728% | 1.4434 | 19.3521 | N/A | 96.1272 | 2.0634 | 78.8004 | Volume from own sources | Customer metering inaccuracies | Unauthorized consumption | 9 | 3 | n/a |  | n/a |  | 9 | 10 | 10 | 5 | 5 | 5 | 5 | 8 | 6 | 10 | 5 | 8 | 9 | 8 |  | Hinesville 2015 Water Audit.xls | 5
Homerville | GA0650000 | CLINCH | 3234 | 145.685 | 0 | 0 | 165.5511 | 117.375 | Note 1 | Note 1 | 2.0694 | 119.4444 | 46.1067 | 10.9138 | 35.1929 | 48.1761 | 45 | 1591 | 45 | 396449 | 3.65 | 106.77 | 7.9185 | 39835.51 | 3757.55 | VPC | 29.1% | 11.05% | 18.7938 | 60.6027 | N/A | 35.1929 | 4.4444 | 42.9139 | Volume from own sources | Billed metered | Customer metering inaccuracies | 2 | 2 | n/a | n/a | n/a |  | 4 | n/a | n/a | 5 | 5 | 2 | 5 | 5 | 6 | 10 | 3 | 10 | 4 | 5 | Bill Powell QWLA # 0030. Met with Joseph Mizell, Water Superintendent, Shirley Teston, City Clerk and Rebecca Mullis, Billing Clerk. | Homerville 2015 Water Audit.xls | 5
Houston County | GA1530021 | HOUSTON | 67746 | 5054.257 | 0 | 0 | 4923.2973 | 3940.521 | 39.54 | 0.56 | 61.5412 | 4042.1622 | 881.1351 | 165.1003 | 716.0348 | 943.2363 | 389.4 | 18668 | 61 | 8064931.31 | 1.77 | 405.41 | 109.2511 | 292227.54 | 290290.01 | VPC | 19.16% | 7.535% | 24.2302 | 105.0857 | N/A | 716.0348 | 6.554 | 55.8625 | Volume from own sources | Customer retail unit cost (applied to Apparent Losses) | Billed metered | 5 | 3 |  | 2.7 |  |  | 6 | 8 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 10 | 3 | 10 | 4 | 5 | QWLA Daniel Walker #0167 All performance indicators are in the correct range. The ILI is up this year, part of which I believe is because of more accurate information. Improved production meter testing is planned for next year, as well as billing rate code formatting which will supply more accurate rate information. | Houston County Worksheet 2015.xls | 5
Jackson County Water and Sewerage Utility | GA1570117 | JACKSON | 19191 | 0 | 1122.534 | 316.706 | 804.4922 | 634.958 | 2.71 | 137.627 | 10.0562 | 785.3512 | 19.1411 | 7.6371 | 11.504 | 166.8242 | 409.99 | 11501 | 104.16 | 7587631 | 5.31 | 2802 | 149.914 | 40552.83 | 32234.22 | VPC | 20.74% | 6.413% | 1.8193 | N/A | 76.8746 | 11.504 | 0.076737 | 71.7573 | Water imported | Billed unmetered | Billed metered | n/a |  | 7 | 5 | 5 | 4 | 6 | 7 | 8 | 5 | 5 | 6 | 5 | 9 | 1 | 10 | 6 | 10 | 9 | 10 | Audit prepared by Joey Leslie, JCWSA Audit validated by Joey Leslie, JCWSA (QWLA # 0073) Financial Data Compiled by Judy Davis, Finance Director JCWSA Customer Retail Unit Cost Spreadsheet by Amy Bales, JCWSA | Jackson Co. 2015 Water Audit.xls | 5
Jasper | GA2270000 | PICKENS | 9850 | 660.73 | 13.914 | 33.681 | 641.1692 | 364.198 | 0 | 7.7899 | 8.0146 | 380.0025 | 261.1666 | 46.1966 | 214.9701 | 276.9712 | 181.5 | 5989 | 70 | 2778468 | 3.25 | 480.42 | 52.3879 | 150138.83 | 103275.92 | VPC | 43.2% | 9.394% | 21.1331 | 98.3401 | N/A | 214.9701 | 4.1034 | 56.5456 | Volume from own sources | Customer metering inaccuracies | Billed metered | 5 | 2 | n/a |  | 3 | 1 | 3 | 6 | 1 | 5 | 5 | 1 | 5 | 2 | 2 | 1 | 1 | 10 | 4 | 10 | QWLA 0071: Spencer Senerman. Lisa Hoyle is the City Clerk/Director of Finance for the City of Jasper. Von Headrick is the Assistant Fire Chief for the City of Jasper. David Hall is the Water Superintendent for the City of Jasper. Rachael Childers is the Utility Clerk/Assistant Tax Clerk for the City of Jasper. When preparing next year's audit, careful consideration should be given to all water supplied and authorized consumption inputs, as several errors were discovered. In particular, the City should verify the water exported input and unbilled metered input are excluded from the billed metered input. This audit indicates Jasper experiences a high amount of water loss. The City should investigate this loss by testing customer meters and looking for leaks in the water system. Additionally, the City should test and calibrate its production meter annually. It should be noted that apparent losses are significantly higher in 2015 when compared to past audits. This is because David's estimate of customer meter inaccuracy was 9.99% compared to previous years, which had a customer meter inaccuracy of 4%. | Jasper, City of Worksheet 2015.xls | 5
Jefferson | GA1570003 | JACKSON | 10501 | 438.5 | 35.1 | 0 | 471.3999 | 381.732 | 0.294 | 17.986 | 5.8925 | 405.9045 | 65.4954 | 10.2903 | 55.2051 | 89.3739 | 120.04 | 4831 | 68 | 2169135 | 9.31 | 605.19 | 34.1043 | 95803.07 | 33409.56 | VPC | 18.96% | 6.623% | 5.8358 | 31.3076 | N/A | 55.2051 | 1.6187 | 71.645 | Volume from own sources | Customer metering inaccuracies | Variable production cost (applied to Real Losses) | 7 | 3 | 5 | 4 | n/a |  | 7 | 8 | 10 | 5 | 5 | 3 | 5 | 5 | 7 | 10 | 3 | 10 | 9 | 3 | Audited by Jeff Killip. QWLA 052 | Jefferson Water Audit 2015.xls | 5
Jesup | GA3050000 | WAYNE | 10200 | 474.38 | 0 | 0 | 480.3848 | 383.1 | Note 1 | 25.689 | 6.0048 | 414.7938 | 65.591 | 14.8017 | 50.7893 | 97.2848 | 134.2 | 5482 | 58.5 | 1003462 | 2.65 | 198.17 | 33.0605 | 39224.43 | 10064.92 | VPC | 20.25% | 5.538% | 7.3974 | 25.3829 | N/A | 50.7893 | 1.5363 | 76.8272 | Variable production cost (applied to Real Losses) | Volume from own sources | Billed metered | 5 | 3 | n/a |  | n/a |  | 6 | n/a | 7 | 5 | 5 | 3 | 5 | 7 | 9 | 10 | 8 | 10 | 5 | 7 |  | Jesup Water Audit 2015.xls | 5
Jones County Water System | GA1690002 | JONES | 10911 | 607.76 | 21.839 | 112.08 | 533.5247 | 288.072 | 0.1 | 8.65 | 6.6691 | 303.4911 | 230.0337 | 31.4001 | 198.6336 | 245.3527 | 158.3 | 4180 | 78 | 1170789 | 3.64 | Note 2 | 42.2325 | 114296.45 | Note 4 | CRUC | 45.99% | 76.28% | 20.5808 | N/A | 3437.7861 | 198.6336 | 4.7033 | 75.7515 | Volume from own sources | Billed metered | Customer metering inaccuracies | 3 | 7 | 3 | 4 | 6 | 8 | 6 | 2 | 2 | 5 | 5 | 5 | 5 | 8 | 9 | 10 | 1 | 10 | 10 | 10 |  | Jones Co 2015 Water Audit.xls | 5
Kings Bay Naval Base | GA0390013 | CAMDEN | 9730 | 268.402 | 0 | 0 | 268.402 | 136.884 | 108.864 | 0 | 3.355 | 249.103 | 19.299 | 2.001 | 17.298 | 22.654 | 100 | 800 | 101 | 760801.46 | 10.21 | 536.9 | 24.9961 | 20430.21 | 9287.28 | VPC | 8.44% | 4.143% | 6.8527 | N/A | 473.9171 | 17.298 | 0.69203 | 72.7941 | Billed metered | Billed unmetered | Customer metering inaccuracies | 9 | 4 | n/a | n/a | n/a |  | 2 | 2 | n/a | 5 | 10 | 3 | 5 | 7 | 10 | 10 | 10 | 10 | 10 | 10 | Bill Powell QWLA # 0030. All supporting documentation will be maintained on site at utilities and energy managers office. This are available for inspection if the EPD wishes to review. Documents are not allowed to leave the base. | USN Kings Bay 2015 Water Audit.xls | 5
Kingsland | GA0390000 | CAMDEN | 18697 | 601.662 | 0 | 0 | 598.6687 | 533.69 | 0 | 1.025 | 7.4834 | 542.1984 | 56.4703 | 8.2321 | 48.2382 | 64.9787 | 179 | 8961 | 62 | 1721706 | 2.28 | 147.51 | 52.3328 | 18769.09 | 7115.62 | VPC | 10.85% | 1.576% | 2.5169 | 14.7483 | N/A | 48.2382 | 0.92176 | 66.401 | Billed metered | Variable production cost (applied to Real Losses) | Unbilled metered | 9 | 3 | n/a |  | n/a |  | 4 | n/a | 6 | 5 | 5 | 5 | 5 | 8 | 4 | 10 | 8 | 6 | 8 | 4 | All comments from QWLA Brian Gaddy. | Kingsland 2015 water audit.xls | 5
LaFayette | GA2950002 | WALKER | 18177 | 712.87 | 360.671 | 0 | 1106.4001 | 683.519 | 0 | 4.427 | 13.83 | 701.776 | 404.6241 | 29.2046 | 375.4195 | 422.8811 | 238.8 | 7996 | 75 | 3115805 | 4.29 | 616.36 | 68.1996 | 125287.95 | 231393.56 | VPC | 38.22% | 11.81% | 10.0066 | 128.6326 | N/A | 375.4195 | 5.5047 | 60.1122 | Volume from own sources | Customer metering inaccuracies | Unbilled metered | 8 | 3 | 7 | 4 | n/a | n/a | 6 | n/a | 5 | 5 | 5 | 3 | 5 | 5 | 6 | 10 | 2 | 8 | 8 | 5 | QWLA: Charles Reynolds 0148 | LaFayette, City of Worksheet 2015.xls | 5
LaGrange | GA2850001 | TROUP | 41852 | 2551.45 | 0 | 150.706 | 2400.744 | 2046.763 | 0 | 0 | 30.0093 | 2076.7723 | 323.9717 | 16.2485 | 307.7232 | 353.981 | 442.69 | 19802 | 89 | 3568958 | 5.17 | 419.59 | 174.2902 | 84004.74 | 129117.58 | VPC | 14.74% | 6.324% | 2.2481 | 42.5754 | N/A | 307.7232 | 1.7656 | 71.2571 | Volume from own sources | Variable production cost (applied to Real Losses) | Unauthorized consumption | 7 | 3 | n/a | n/a | 9 | 3 | 8 | n/a | n/a | 5 | 5 | 7 | 5 | 8 | 6 | 10 | 5 | 10 | 5 | 5 | QWLA Keith Hester 0140 evaluated audit. Information here in proves to be accurate. Target areas for improvement have noted and will begin addressing in the coming year. ILI 2.49 | LaGrange 2015 water audit.xls | 5
Larchmont Utilities | GA0510034 | CHATHAM | 11799 | 363.67 | 0 | 0 | 363.67 | 313.49 | 0 | 1.676 | 4.5459 | 319.7119 | 43.9581 | 2.4828 | 41.4753 | 50.18 | 55.96 | 5440 | 53 | 1547524 | 4.35 | 222 | 21.6421 | 10800.14 | 9207.52 | VPC | 13.8% | 1.382% | 1.2504 | 20.8881 | N/A | 41.4753 | 1.9164 | 55.3529 | Volume from own sources | Total annual cost of operating water system | Unbilled metered | 7 | 3 | n/a |  | n/a |  | 2 | n/a | 3 | 5 | 5 | 5 | 1 | 4 | 4 | 7 | 5 | 5 | 5 | 6 |  | Larchmont Utilities Worksheet 2015.xls | 4.2
Lavonia | GA1190003 | FRANKLIN | 8190 | 440.33 | 27.88 | 114.179 | 334.6845 | 204.531 | 0.016 | 19.095 | 4.1836 | 227.8256 | 106.8589 | 3.6069 | 103.252 | 130.1375 | 127 | 3513 | 107 | 1394775 | 5 | 572.84 | 47.4136 | 18034.44 | 59146.9 | VPC | 38.88% | 6.49% | 2.8129 | N/A | 2227.4198 | 103.252 | 2.1777 | 63.6776 | Volume from own sources | Water exported | Unauthorized consumption | 5 | 3 | 9 | 3 | 9 | 3 | 9 | 4 | 5 | 5 | 5 | 7 | 5 | 5 | 6 | 10 | 3 | 10 | 7 | 5 | QWLA- Martin D. Eckles Sr., QWLA Certification # 0168 | Lavonia, City of Worksheet 2015.xls | 5
Lawrenceville Water Department | GA1350005 | GWINNETT | 30000 | 135.69 | 661.005 | 5.896 | 796.7324 | 746.888 | Note 1 | 12.518 | 9.9592 | 769.3652 | 27.3673 | 19.3571 | 8.0101 | 49.8444 | 100 | 8151 | 100 | 4938000 | 6.31 | 4051.83 | 64.3732 | 122143.51 | 32455.7 | VPC | 6.256% | 4.975% | 6.5063 | 2.6924 | N/A | 8.0101 | 0.12443 | 67.5407 | Water imported | Variable production cost (applied to Real Losses) | Volume from own sources | 3 | 4 | 8 | 3 | 8 | 3 | 8 | n/a | 7 | 5 | 5 | 7 | 5 | 3 | 8 | 10 | 5 | 10 | 8 | 4 | The water system uses @ 2 MG per day over the last 10 years. Production from two plants that are supplied by seven wells average @ 400,000 gallons per day. The balance is purchased at a rate of $4.85 per 1,000 gallons from Gwinnett County. | Lawrenceville Water Dept Worksheet 2015.xls | 5
Lee County Utilities Authorty | GA1770068 | LEE | 13887 | 586.394 | 0 | 0 | 586.394 | 526.885 | 0 | 1.605 | 7.3299 | 535.8199 | 50.5741 | 21.9512 | 28.6228 | 59.509 | 77 | 5525 | 68 | 1742500 | 1.97 | 266.89 | 30.9088 | 43243.92 | 7639.15 | VPC | 10.15% | 3.057% | 10.8851 | 14.1934 | N/A | 28.6228 | 0.92604 | 54.7157 | Volume from own sources | Customer metering inaccuracies | Unbilled metered | 5 | 3 | n/a |  | n/a |  | 7 | n/a | 9 | 5 | 5 | 6 | 5 | 7 | 7 | 10 | 5 | 10 | 6 | 5 | QWLA: Tal Woodall. All informetion was provided and verified by Chris Boswell, Genreal Manager, Lee County Utilies Authority. All performance indicators are outside of there expected range. The real and apparent losses are both low and the ILI is extremely low. These are most likely th result of under registering production meters. The system was advised to have a ll production meters tested for accuracy and calibrated or replaced as needed. The system was also advised to consider tracking water and sewer expenses seperately | Lee County Worksheet 2015.xls | 5
Lincoln County Water System | GA1810038 | LINCOLN | 5312 | 12.061 | 92.011 | 0 | 107.2907 | 54.0368 | 0 | 0.0005 | 1.3411 | 55.3785 | 51.9123 | 1.5061 | 50.4061 | 53.2539 | 128.6 | 2034 | 82 | 682071 | 8.76 | 1581 | 29.9547 | 13193.62 | 79692.12 | VPC | 49.64% | 13.93% | 2.0287 | N/A | 1073.8649 | 50.4061 | 1.6827 | 52.6859 | Water imported | Unbilled metered | Billed metered | 4 | 2 | 1 | 1 | n/a |  | 3 | n/a | n/a | 5 | 5 | 2 | 5 | 8 | 6 | 10 | 1 | 10 | 8 | 10 | Certification of water audit occurred on 24 March 2016. In attendance from County: Director of Public Works and the Administrative Assistant for the Public Works Department. Qualified water audit staff: Mr. Fletcher Holliday and Mrs. Chris Hinson. The low service connectioin density (16 connections/mile) does not alllow for a calculation of water loss per service connection per day. | Lincoln County Worksheet 2015.xls | 5
Locust Grove | GA1510002 | HENRY | 5648 | 164.874 | 33.604 | 0 | 208.5501 | 156.028 | 0 | 0.993 | 2.6069 | 159.6279 | 48.9222 | 2.8991 | 46.0231 | 52.5221 | 43 | 2400 | 60 | 1518372 | 10.39 | 1023.07 | 12.9786 | 30121.16 | 47084.89 | VPC | 25.18% | 5.327% | 3.3094 | 52.5378 | N/A | 46.0231 | 3.5461 | 56.8713 | Volume from own sources | Unbilled metered | Customer metering inaccuracies | 4 | 2 | 9 | 1 | n/a |  | 4 | n/a | 1 | 5 | 5 | 2 | 5 | 4 | 5 | 10 | 2 | 10 | 9 | 10 | Auditor: Spencer Senerman, QWLA 0071: Spencer Senerman. Tim Young is the City Manager for the City of Locust Grove. Jon Holland is the Utilities Manager for the City of Locust Grove. Jenny Merritt is a Clerk in the City of Locust Grove's billing department. Jeff Benton is a Customer Accounts Supervisor for the Henry County Water Authority's Billing Department. General Recommendations: The City of Locust Grove should test all production meters for accuracy on a yearly basis. The meters should be calibrated on a yearly basis as well. The City should also test approximately 1% of its customer meters (25 meters) to obtain a better understanding of how accurate its customer meters are. | Locust Grove, City of Worksheet 2015.xls | 5
Loganville Water Department | GA1350006 | WALTON | 10923 | 0 | 401.52 | 0 | 401.52 | 381.54 | 4 | 3 | 5.019 | 393.559 | 7.961 | 2.3426 | 5.6184 | 15.98 | 82.4 | 5400 | 80 | 3000000 | 8.4 | 3 | 36.6689 | 19677.63 | 16.86 | VPC | 3.98% | 0.6573% | 1.1885 | 2.8505 | N/A | 5.6184 | 0.15322 | 70.0789 | Water imported | Billed unmetered | Customer metering inaccuracies | n/a | n/a | 8 | n/a | n/a | n/a | 7 | 5 | 6 | 5 | 5 | 3 | 5 | 9 | 9 | 10 | 8 | 8 | 4 | 10 |  | Loganville 2015 water audit.xls | 5
Lowndes County - North | GA1850016 | LOWNDES | 6430 | 532.05 | 0.193 | 0 | 505.2238 | 252.1 | 0.274 | 0 | 6.3153 | 258.6893 | 246.5346 | 1.8933 | 244.6412 | 252.8498 | 76.2 | 2719 | 61 | 583200 | 5.75 | 524.25 | 18.2593 | 10886.53 | 128253.17 | VPC | 50.05% | 24.43% | 1.9077 | 246.5061 | N/A | 244.6412 | 13.3981 | 61.488 | Volume from own sources | Total annual cost of operating water system | Variable production cost (applied to Real Losses) | 6 | 3 | 5 |  | n/a |  | 7 | 10 | n/a | 5 | 5 | n/a | 5 | 8 | 6 | 10 | 3 | 5 | 6 | 5 | QWLA: Brandon Rice #0038 rice.brandon79@yahoo.com 229-539-6976 | North Lowndes Worksheet 2015.xls | 5
Lowndes County - South | GA1850019 | LOWNDES | 5957 | 350.48 | 0 | 0 | 372.8511 | 239.8 | 0 | 3.01 | 4.6606 | 247.4706 | 125.3804 | 1.5316 | 123.8488 | 133.0511 | 82 | 2617 | 61 | 578340 | 5.75 | 621.05 | 18.6173 | 8806.86 | 76916.3 | VPC | 35.68% | 15.65% | 1.6035 | N/A | 4137.9485 | 123.8488 | 6.6523 | 57.0945 | Volume from own sources | Unbilled metered | Total annual cost of operating water system | 6 | 3 | n/a |  | n/a |  | 7 | n/a | 5 | 5 | 5 | n/a | 5 | 8 | 6 | 10 | 3 | 5 | 6 | 5 | QWLA: Brandon Rice #0038 rice.brandon79@yahoo.com 229-539-6976 | South Lowndes 2015 Water Audit.xls | 5
Macon Water Authority | GA0210001 | BIBB | 130024 | 8671.38 | 0 | 246.06 | 7905.0372 | 6782.12 | 0 | 105.67 | 53.94 | 6941.73 | 963.3072 | 89.5239 | 873.7833 | 1122.9172 | 1391.6 | 63338 | 125.3 | 16197450 | 4.07 | 672.84 | 778.8245 | 487081.32 | 587914.63 | VPC | 14.21% | 7.3% | 3.8724 | 37.7961 | N/A | 873.7833 | 1.1219 | 88.8785 | Volume from own sources | Billed metered | Customer metering inaccuracies | 9 | 3 | n/a |  | 6 |  | 8 | n/a | 10 | 8 | 8 | 8 | 8 | 9 | 10 | 10 | 7 | 10 | 10 | 10 | QWLA: Heather Veal # 0036. See the 2015_MWA_Basis of Audit Summary for notes. [CRUC converted: $/100 cubic feet (ccf) to $/1000 gallons (US)] | Macon 2015 Water Audit.xls | 5
Madison | GA2110002 | MORGAN | 5215 | 471.132 | 0 | 13.618 | 443.5843 | 352.091 | 0 | 20.86 | 5.5448 | 378.4958 | 65.0885 | 11.552 | 53.5365 | 91.4933 | 75 | 2851 | 60 | 2984234 | 6.3 | 500.74 | 18.2515 | 72777.82 | 26807.86 | VPC | 20.63% | 3.78% | 11.1012 | 51.447 | N/A | 53.5365 | 2.9333 | 64.8352 | Volume from own sources | Variable production cost (applied to Real Losses) | Customer retail unit cost (applied to Apparent Losses) | 5 | 3 | n/a |  | 5 | 1 | 9 | n/a | 9 | 5 | 5 | 8 | 5 | 8 | 7 | 10 | 3 | 10 | 6 | 5 | QWLA: Tal Woodall - All of the inputs and supporting documents were reviewed and verified with Chief Operator, Larry Stephens. The notable performance indictors are within their expected ranges; however, these values are low and suspect due to estimations made througout the audit. It is recommended for the raw, treated, and finshed water meters, as well as, the export be tested and/or calibrated and the test results kept on file. It is also recommended for the export meters to be read on a daily basis. | Madison WaterAudit 2015.xls | 5
Manchester Water Works | GA1990003 | MERIWETHER | 5343 | 466.11 | 0 | 101.22 | 364.89 | 110.7 | Note 1 | 105.6 | 4.5611 | 220.8611 | 144.0289 | 24.9556 | 119.0733 | 254.19 | 113 | 2359 | 66 | 1791245 | 5.71 | 590.1 | 23.2512 | 142496.29 | 70265.16 | VPC | 69.66% | 15.51% | 28.9832 | N/A | 2886.9756 | 119.0733 | 5.1212 | 60.6403 | Unbilled metered | Customer metering inaccuracies | Billed metered | 8 | 1 | n/a | n/a | 7 | 1 | 4 | n/a | 1 | 5 | 5 | 1 | 5 | 2 | 2 | 10 | 2 | 10 | 6 | 10 | Audit Prepared By: James C. Stephens (706) 977-6981 cell (706) 846-4384 wtswtreatmentdirector@manchester-ga.gov QWLA: ID# 0064 James C. Stephens, City of Manchester, Water and Sewer Treatment Director (706) 977-6981 wtswtreatmentdirector@manchester-ga.gov | Manchester 2015 Water Audit.xls | 5
Marietta Board of Lights and Water | GA0670005 | COBB | 60100 | 0 | 2918.773 | 0 | 2918.773 | 2583.089 | Note 1 | Note 1 | 36.4847 | 2619.5737 | 299.1993 | 39.8465 | 259.3529 | 335.684 | 348.1 | 18199 | 87 | 21611556 | 7.43 | 2788.67 | 146.4881 | 296059.22 | 723249.58 | VPC | 11.5% | 5.187% | 5.9986 | 39.0437 | N/A | 259.3529 | 1.7705 | 79.7444 | Water imported | Billed metered | Unauthorized consumption |  |  | 9 | 5 |  |  | 7 | 7 | 7 | 5 | 5 | 7 | 5 | 8 | 6 | 10 | 5 | 9 | 8 | 10 | Auditor and QWLA: Thomas B Jones #0075. All supporting documentation is either maintained by the auditor or available to the auditor through shared database systems. | Marietta Board of Lights and Water Worksheet 2015.xls | 5
McCaysville Water | GA1110001 | FANNIN | 7020 | 284.66 | 0.57791 | 42.03 | 241.2622 | 117.99 | Note 1 | 1.4001 | 3.0158 | 122.4059 | 118.8563 | 2.1041 | 116.7522 | 123.2722 | 150 | 3350 | 89 | 1545300.78 | 5.75 | 833.04 | 42.6853 | 12098.52 | 97259.27 | VPC | 51.09% | 7.315% | 1.7208 | N/A | 2132.4607 | 116.7522 | 2.7352 | 66.6778 | Volume from own sources | Customer metering inaccuracies | Billed metered | 6 | 3 | 4 | 1 | 5 | 1 | 5 | n/a | 9 | 5 | 5 | 3 | 5 | 3 | 2 | 10 | 2 | 10 | 8 | 4 | (QWLA # 0156; Davy Ensley; Contact # 706-492-4921; Email, mcityhall@etcmail.com; Auditer, Davy Ensley). System needs to get written policies for water import and export meter testing. Also needs to expand on meter accuracy testing, on small customer meters, and needs to get data for water plant master meter. | McCaysville 2015 water aduit.xls | 5
McDonough | GA1510003 | HENRY | 8962 | 431.793 | 1.384 | 0 | 417.2991 | 278.589 | 0 | 9.75 | 5.2162 | 293.5552 | 123.7439 | 4.6522 | 119.0916 | 138.7101 | 90 | 6200 | 78.42 | 2536092 | 4.68 | 510.46 | 40.5564 | 21772.46 | 60791.52 | VPC | 33.24% | 3.557% | 2.0558 | 52.6256 | N/A | 119.0916 | 2.9364 | 49.4507 | Volume from own sources | Unbilled metered | Customer metering inaccuracies | 5 | 5 | 9 | 1 | n/a | n/a | 5 | n/a | 3 | 5 | 5 | 3 | 7 | 3 | 5 | 10 | 5 | 10 | 10 | 7 | QWLA: Patrick L. Kelley [678-583-3827]; QWLA Registry Number: 0069 Utility Name: City of McDonough; PWS ID#: GA1510003; Audit Preparer: Steve Cox Water Loss Audit Year: 2015 Calendar Year General Notes: The City of McDonough operates it's own Water Treatment Plant that is supplemented by 3 wells (2 active; 1 inactive). Imported water accounts for approximately 9% of the overall volume. | McDonough, City of Worksheet 2015-Peter.xls | 5
McRae Water System | GA2710003 | TELFAIR | 5488 | 234.643 | 0 | 0 | 228.7415 | 189.485 | 0 | 3.326 | 2.8593 | 195.6703 | 33.0712 | 7.5224 | 25.5488 | 39.2565 | 45 | 1813 | 56 | 340966 | 2.67 | 149.12 | 10.5348 | 20084.87 | 3809.83 | VPC | 17.16% | 7.278% | 11.3676 | 38.6082 | N/A | 25.5488 | 2.4252 | 44.8928 | Volume from own sources | Unbilled metered | Customer metering inaccuracies | 5 | 2 | n/a |  | n/a |  | 5 | n/a | 7 | 5 | 5 | 6 | 5 | 5 | 8 | 10 | 3 | 5 | 5 | 3 | The City of McRae-Helena operates two water systems: "McRae" and "Helena." The Helena system provides water to a population less than 3,300. Some values such as operating costs had to be estimated based on the amount of water produced in each system. (METER MALFUNCTION, METER REPLACED, ACTUAL VOLUME WAS ESTIMATED FOR 3-4 MONTHS) QWLA: Tal Woodall -- All inputs and supporting documents were discussed and verified with the City Clerk, Liz McLean and Public Works Director, Andy Dykes. The resulting performance indicators are all low and/or below the expected range. This is most likely the result of an understated Water Supplied Volume due to a production meter malfunction which has since been replaced. It is recommended to have all source meters tested on a regular basis and calibrated or replaced as needed. | McRae, City of Worksheet 2015.xls | 5
Metter | GA0430000 | CANDLER | 4776 | 146.24 | 0 | 0 | 150.7629 | 141.428 | Note 1 | 2.83 | 1.8845 | 146.1425 | 4.6204 | 3.6745 | 0.94583 | 9.3349 | 56.2 | 2173 | 65 | 540967 | 3.87 | 263.81 | 14.9466 | 14220.38 | 249.52 | VPC | 6.192% | 2.905% | 4.6328 | 1.1925 | N/A | 0.94583 | 0.063281 | 62.6687 | Volume from own sources | Billed metered | Customer metering inaccuracies | 5 | 2 | n/a |  | n/a |  | 7 | n/a | 7 | 5 | 5 | 5 | 5 | 6 | 7 | 10 | 3 | 10 | 7 | 7 | QWLA: Melissa Edenfield #0157-Discussed all information provided with the Public Works Director during audit. | Metter 2015 Water Audit.xls | 5
Milledgeville | GA0090001 | BALDWIN | 19456 | 1392.99 | 0 | 0 | 1402.6684 | 846.604 | 241.318 | 0.863 | 52.997 | 1141.782 | 260.8864 | 14.1835 | 246.703 | 314.7464 | 200.6 | 7718 | 80 | 3959052.49 | 4.21 | 429.65 | 65.494 | 59712.34 | 105995.93 | VPC | 22.44% | 4.77% | 5.0348 | 87.5743 | N/A | 246.703 | 3.7668 | 55.5088 | Volume from own sources | Billed unmetered | Customer metering inaccuracies | 5 | 4 | n/a |  | n/a |  | 8 | 4 | 6 | 5 | 5 | 5 | 5 | 5 | 6 | 10 | 7 | 8 | 6 | 6 |  | Milledgeville 2015 Water Audit.xls | 5
Millen | GA1650000 | JENKINS | 4000 | 172.687 | 0 | 0 | 178.0278 | 146.195 | 0 | 5.459 | 1.606 | 153.26 | 24.7678 | 7.1295 | 17.6384 | 31.8328 | 80 | 4212 | 60 | 212084 | 2.05 | 346.28 | 23.3147 | 14615.42 | 6107.81 | VPC | 17.88% | 10.92% | 4.6374 | 11.473 | N/A | 17.6384 | 0.75653 | 46.9334 | Volume from own sources | Customer metering inaccuracies | Variable production cost (applied to Real Losses) | 4 | 2 | n/a |  | n/a |  | 5 | n/a | 9 | 10 | 5 | 3 | 5 | 5 | 7 | 10 | 4 | 4 | 5 | 3 |  | Millen, City of Worksheet 2015.xls | 5
Monroe | GA2970001 | WALTON | 23376 | 913.16 | 0 | 64.642 | 848.785 | 607.598 | 9.13 | Note 1 | 10.6098 | 627.3378 | 221.4472 | 8.2324 | 213.2148 | 232.057 | 214 | 10633 | 60 | 1889071.17 | 7.25 | 531.65 | 60.2839 | 59684.74 | 113355.65 | VPC | 27.34% | 9.459% | 2.1212 | 54.9375 | N/A | 213.2148 | 3.5368 | 69.918 | Volume from own sources | Billed metered | Variable production cost (applied to Real Losses) | 8 | 4 |  |  | 3 | 1 | 6 | 6 | 10 | 5 | 5 | 7 | 10 | 9 | 9 | 10 | 1 | 10 | 8 | 6 | QWLA Comments - 80% of Monroe's distribution system is PVC, and Monroe's experience is that water main breaks are at a minimum. QWLS recommends that a hydraulic water model of Monroe's distribution system be prepared. | Monroe, City of Worksheet 2015.xls | 5
Montezuma | GA1930002 | MACON | 3443 | 138.372 | 0 | 0 | 138.372 | 102.963 | 0.288 | 0 | 1.7297 | 104.9806 | 33.3914 | 6.0224 | 27.3689 | 35.121 | 38 | 1947 | 55 | 441179.85 | 4 | 368.67 | 9.9899 | 24089.77 | 10090.1 | VPC | 25.38% | 7.892% | 8.4745 | 38.5122 | N/A | 27.3689 | 2.7397 | 54.7745 | Volume from own sources | Billed metered | Billed unmetered | 2 | 2 | n/a |  | n/a |  | 4 | 2 | n/a | 5 | 5 | 2 | 5 | 2 | 6 | 10 | 2 | 8 | 8 | 5 | Bill Powell, QWLA 0030. Working with Jim Copland, water and wastewater superintendent. | Montezuma, City of Worksheet 2015.xls | 5
Monticello | GA1590000 | JASPER | 3505 | 165.57 | 0 | 0 | 162.3235 | 114.1 | Note 1 | 21.14 | 2.029 | 137.269 | 25.0545 | 7.809 | 17.2455 | 48.2235 | 29.5 | 2078 | 80 | 862178.43 | 5.14 | 798.08 | 13.7618 | 40138.02 | 13763.31 | VPC | 29.71% | 8.396% | 10.2957 | 22.7373 | N/A | 17.2455 | 1.2531 | 43.5686 | Volume from own sources | Unbilled metered | Customer metering inaccuracies | 7 | 2 |  |  |  |  | 6 |  | 2 | 5 | 5 | 3 | 5 | 8 | 5 | 10 | 6 | 10 | 3 | 5 | QWLA #0118- Waymon Cody conducts this water audit with Peggy Billerman (City Manager) Lathaydra Sands (City Clerk) and Dieone Pennamon (Billing and records keeper) | Monticello 2015 Water Audit.xls | 5
Moultrie Utilities | GA0710004 | COLQUITT | 15049 | 867.48 | 0 | 0 | 868.48 | 707.647 | 0 | 4.712 | 10.856 | 723.215 | 145.265 | 18.4783 | 126.7867 | 160.833 | 219.48 | 7203 | 65 | 1490688 | 2.4 | 335.85 | 53.8044 | 44347.82 | 42581.33 | VPC | 18.52% | 6.182% | 7.0284 | 48.2245 | N/A | 126.7867 | 2.3564 | 59.8057 | Volume from own sources | Customer metering inaccuracies | Variable production cost (applied to Real Losses) | 5 | 3 | n/a |  | n/a |  | 7 | n/a | 7 | 5 | 5 | 5 | 5 | 9 | 8 | 10 | 6 | 10 | 6 | 5 | QWLA: The City of Moultrie 2015 audit performance indicators for normalized and apparent losses fall in line with the state averages. The customer retail unit and the variable production costs are slightly low, as you would expect for a groundwater well system. The ILI is also right about average for the state. Grading could be improved next year by inacting a meter accuracy testing program for both production and customer meters. | Moultrie 2015 Water Audit.xls | 5
Nashville | GA0190002 | BERRIEN | 4680 | 200.789 | 0 | 0 | 223.0989 | 185.375 | Note 1 | 0.238 | 2.7887 | 188.4017 | 34.6972 | 10.7903 | 23.9069 | 37.7239 | 85 | 2300 | 60 | 575000 | 1.75 | 0.35 | 17.6262 | 18883.01 | 8.37 | VPC | 16.91% | 3.286% | 12.8532 | N/A | 770.5677 | 23.9069 | 1.3563 | 39.5597 | Volume from own sources | Total annual cost of operating water system | Billed metered | 3 | 1 | n/a |  | n/a |  | 5 | n/a | 5 | 5 | 5 | 5 | 5 | 4 | 7 | 10 | 1 | 3 | 4 | 4 | QWLA Brandon Rice 0038 rice.brandon79@yahoo.com 2295396976 | Nashville water audit 2015.xls | 5
Newnan / Newnan Utilities | GA0770002 | COWETA | 34000 | 2424.33 | 52.34 | 1152.41 | 1324.5812 | 1145.756 | 0 | 74.93 | 16.5573 | 1237.2433 | 87.338 | 6.1758 | 81.1621 | 178.8252 | 254.1 | 21054 | 85 | 9179603 | 6.49 | 416.25 | 140.6295 | 40081.22 | 33783.73 | VPC | 13.5% | 1.22% | 0.80365 | 10.5615 | N/A | 81.1621 | 0.57713 | 73.5686 | Volume from own sources | Customer metering inaccuracies | Variable production cost (applied to Real Losses) | 7 | 5 | 5 | 7 | 7 | 7 | 9 | n/a | 9 | 5 | 5 | 9 | 5 | 10 | 10 | 10 | 10 | 10 | 9 | 7 | Contributors: Jenny Paul, DeeAnn Boone, Randy Crawford, Erin Jefts, Scott Tolar, Jeff Pecce, George Lee, Coweta County Water. 770-683-5516 QWLA Comments - Newnan Utilities has a tight water distribution system with the ILI being less than one. Newnan Utilities only allows ductile iron water pipe installed in its distribution system, and this has been the policy since at least 1980. Newnan Utilities has a 5-year program in place to replace all galvinized water pipe. Newnan Utilities is in year 3 of this program, and the program is on schedule. Recommend that Venturi meters at WTP are tested hydraulically for meter accuracy. This has never been done. This may explain the low ILI. Also, test all meters to and from Coweta County Water & Sewer Authority for meter accuracy of the flow element. | Newnan Utilities Worksheet 2015.xls | 5
Newton County Water and Sewerage Authority | GA2170004 | NEWTON | 60635 | 0 | 5798.372 | 3912.022 | 1865.0822 | 1702.82 | Note 1 | Note 1 | 23.3135 | 1726.1335 | 138.9487 | 43.6712 | 95.2775 | 162.2622 | 625 | 27684 | 107.75 | 7461467.06 | 7.49 | 2160 | 296.2969 | 327097.17 | 205799.44 | VPC | 8.7% | 7.817% | 4.3219 | 9.4291 | N/A | 95.2775 | 0.32156 | 75.136 | Water imported | Unauthorized consumption | Systematic data handling errors |  | 6 | 6 | 4 | 9 | 7 | 8 |  |  | 5 | 5 | 8 | 5 | 8 | 8 | 10 | 7 | 8 | 8 | 10 | The Newton County Water and Sewerage Authority is billed by the Newton County Board of Commissioners for its wholesale water use. The NCBOC also bills eight different entities in the county whom the Authority distributes water to each of them (No Charge). NCWSA’s water source is Lake Varner and the Cornish Creek Water Treatment Plant. The water is treated and discharged out of the plant and goes through their production meter located on the WTP site from which we are billed from (we have no information on the meter other than it is a Mag meter or Electromagnetic Meter). We have been told that the electrical components of this meter are tested on an annual basis, but the meter is not capable of being flow tested (it does not have a testing port). After passing through this meter the water is now in our distribution system and is distributed IN and Out of the eight different entities making up the Newton County Consecutive System going through 52 different master meters during the process. NEWTON COUNTY WATER AND SEWRAGE AUTHORITY DO NOT OWN THE SOURCE OR THE MASTER METERS. QWLA - The ILI is low but Newton County Water Authority has a very unusual system. They also have a very aggressive meter replacement program and a leak detection program. They are working to improve their data inputs on water supply and master meter error adjustments but they have to work with what they are provided by their wholesaler. | Newton County Water and Sewerage Auth 2015 (2170097).xls | 5
North Fulton County | GA1210005 | FULTON | 172533 | 0 | 11231.388 | 131.7085 | 11086.2694 | 10116.8687 | Note 1 | Note 1 | 138.5784 | 10255.447 | 830.8224 | 239.943 | 590.8794 | 969.4007 | 1149.04 | 74441 | 97.4 | 33880033.29 | 3.35 | 575.22 | 617.9637 | 803536.83 | 339883.45 | VPC | 8.744% | 3.61% | 8.8309 | 21.7467 | N/A | 590.8794 | 0.95617 | 69.8473 | Water imported | Variable production cost (applied to Real Losses) | Billed metered |  |  | 7 | 5 | 7 | 7 | 7 |  |  | 5 | 5 | 6 | 5 | 8 | 6 | 10 | 9 | 10 | 9 | 5 | QWLA: All "must have" documentation provided. Initial review of metrics appear to be within range. Post audit review of metrics show small differences but still within range. Small reduction of validity score from 72 to 70. | North Fulton County Worksheet 2015.xls | 5
Notla Water Authority | GA2910003 | UNION | 13465 | 331.587 | 0 | 0 | 331.587 | 215.026 | 0 | 4.857 | 4.1448 | 224.0278 | 107.5592 | 6.9235 | 100.6356 | 116.561 | 525 | 5770 | 90 | 2162259 | 8.5 | 563.03 | 121.7339 | 58850.03 | 56660.88 | VPC | 35.15% | 5.577% | 3.2874 | N/A | 525.1696 | 100.6356 | 0.82669 | 59.951 | Volume from own sources | Billed metered | Customer metering inaccuracies | 3 | 3 | n/a |  | n/a |  | 5 | n/a | 9 | 5 | 5 | 3 | 5 | 7 | 5 | 10 | 1 | 10 | 9 | 10 | QWLA 0071: Spencer Senerman. General Manager of the NOTLA Water Authority is Danny Young. Ramona Campbell works in the accounting department for NOTLA Water Authority. Brenda Harwood is the Office Administrator for the NOTLA Water Authority. Jennifer Maier is the laboratory supervisor for the NOTLA Water Authority. Rose Panter works with the CPA who audits NOTLA Water Authority. General Comments: Apparent losses appear high in 2015 because of high Encoder Receiver Transmitter (ERT) error on radio read meters. This increased annual cost of apparent losses. The auditor should double check all consumption inputs next year, as QWLA found double counting of billed metered and unbilled metered volumes. Additionally, any future ERT errors should be included in the customer meter inaccuracy input. NOTLA's ILI is below 1 due to the extremely low connection density (5,679 connections for 500 miles of water main). NOTLA should NOT use this performance indicator to assess its system. Instead, NOTLA should use real losses in gallons/mile/day and apparent losses in gallons/connection/day to assess performance. | Notla Water Auth Worksheet 2015.xls | 5
Oconee County - Watkinson Utility Dept. | GA2150000 | OCONEE | 21897 | 56.092 | 1031.677 | 30.617 | 1084.1252 | 949.214 | 0 | 12.5 | 13.5516 | 975.2656 | 108.8596 | 24.7102 | 84.1494 | 134.9112 | 290 | 13465 | 72 | 2569911 | 7.66 | 1091 | 94.3097 | 189279.86 | 91807.02 | VPC | 12.44% | 12.04% | 5.0278 | 17.1219 | N/A | 84.1494 | 0.89227 | 62.6097 | Water imported | Unbilled metered | Customer metering inaccuracies | 3 | 3 | 5 | 5 | 5 | 5 | 8 | 5 | 5 | 5 | 5 | 6 | 5 | 8 | 8 | 10 | 5 | 7 | 7 | 7 | QWLA - Donald M. Baughcum dbaughcum@oconee.ga.us | Oconee 2015 Water Audit.xls | 5
Oglethorpe | GA1930003 | MACON | 4048 | 194.065 | 0 | 0 | 194.065 | 184.693 | 0 | 1.991 | 2.4258 | 189.1098 | 4.9552 | 2.8326 | 2.1226 | 9.372 | 48 | 1527 | 60 | 286056 | 0.39 | 175 | 10.7032 | 1095.08 | 820.6 | CRUC | 4.829% | 1.267% | 5.0822 | N/A | 121.1527 | 2.1226 | 0.19831 | 68.0196 | Volume from own sources | Total annual cost of operating water system | Customer metering inaccuracies | 8 | 3 | n/a |  | n/a |  | 8 | 7 | 8 | 5 | 5 | 6 | 5 | 4 | 6 | 10 | 5 | 4 | 6 | 6 | Water audit was prepared by Gary Garretson, P.E. and Elmo Richardson, P.E. of Richardson, Garretson and Associates, LLC. Water audit was reviewed by Bill Powell QWLA # 00030. Mr. Powell did not directly talk to Mr. Cannon, water supintendent, or Ms. Levie, city clerk, but reviewed the information provided. Being there is a state prison being served by the city each inmate is counted in the population. Therefore, using EPD's calculation of 2.6 people per connection generates 677 connections would be correct. After talking to Mr. Richardson, reviewing all documentation and correcting the number of connections, the audit for the City of Oglethrope seems to be satisfactory. | Oglethorpe, City of Worksheet 2015.xls | 5
Palmetto | GA1210008 | FULTON | 3965 | 108.69 | 24.832 | 0 | 132.4459 | 98.59 | 0 | 0.38 | 1.6556 | 100.6256 | 31.8203 | 3.1153 | 28.705 | 33.8559 | 34.5 | 1651 | 55 | 968466.05 | 4.54 | 1228.07 | Note 3 | 14143.38 | 35251.76 | VPC | 25.56% | 5.358% | 5.1696 | 47.6341 | N/A | 28.705 | Note 3 | 58.6384 | Volume from own sources | Billed metered | Customer metering inaccuracies | 5 | 4 | 5 |  | n/a |  | 4 | n/a | 8 | 5 | 5 | 3 | 6 | 5 | 4 | 10 | 7 | 10 | 8 | 10 | PWS ID: GA1210008 Converted from 4.2 to v5 | Palmetto, City of Worksheet 2015.xls | 4.2
Paulding County Water System | GA2230002 | PAULDING | 117468 | 0 | 4220.847 | 279.251 | 3906.6657 | 2804.919 | 0 | 14.27 | 48.8333 | 2868.0223 | 1038.6434 | 134.2452 | 904.3982 | 1101.7467 | 980 | 54883 | 99 | 27534413.48 | 6.91 | 3090 | 489.0601 | 927634.13 | 6249391.85 | CRUC | 28.2% | 27.65% | 6.7014 | 45.147 | N/A | 904.3982 | 1.8493 | 79.0282 | Customer metering inaccuracies | Water imported | Billed metered | n/a | n/a | 9 | 1 | 9 | 1 | 7 | n/a | 8 | 5 | 5 | 4 | 5 | 3 | 5 | 10 | 5 | 10 | 8 | 10 |  | Paulding 2015 Water Audit.xls | 5
Pelham | GA2050003 | MITCHELL | 3575 | 202.404 | 0 | 0 | 238.834 | 106.724 | Note 1 | 0.867 | 2.9854 | 110.5764 | 128.2576 | 6.5266 | 121.731 | 132.11 | 47 | 2146 | 62 | 185196 | 2.3 | 313.32 | 13.0387 | 15011.13 | 38140.73 | VPC | 55.31% | 29.35% | 8.3323 | 155.4099 | N/A | 121.731 | 9.3361 | 52.5588 | Volume from own sources | Billed metered | Customer metering inaccuracies | 3 | 3 | n/a |  | n/a |  | 6 | n/a | 6 | 5 | 5 | 1 | 5 | 6 | 3 | 10 | 2 | 10 | 10 | 5 | Gary Boley QWLA # 0029 Feb 29, 2016 | Pelham 2015 Water Audit.xls | 5
Perry | GA1530006 | HOUSTON | 14267 | 745.9 | 0 | 0 | 761.1224 | 552.555 | 0.006 | Note 1 | 9.514 | 562.075 | 199.0474 | 8.8656 | 190.1819 | 208.5614 | 149 | 8063 | 50 | 538900 | 3.42 | 155.18 | 36.7836 | 30320.21 | 29512.42 | VPC | 27.4% | 11.38% | 3.0124 | 64.6219 | N/A | 190.1819 | 5.1703 | 62.8431 | Volume from own sources | Billed metered | Customer metering inaccuracies | 7 | 3 | n/a |  | n/a |  | 7 | 8 | n/a | 5 | 5 | 5 | 5 | 8 | 6 | 10 | 5 | 6 | 6 | 5 | QWLA: The audit falls in line with past years' data with slightly more water produced and consumed in 2015 than in 2014. Grading score has remained the same over several years. Performance Indicators show that apparent losses are somewhat low while real losses are elevated compared to median or average values. This makes sense as the City has made strides in the accounting system over the past 5 years in an attempt to find non-revenue water. Unfortunately, more work remains to improve real losses. Improvement in grade can occur by beginning meter accuracy testing on production and additional customer meters. | Perry 2015 Water Audit.xls | 5
Pickens County | GA2270002 | PICKENS | 6357 | 0 | 225.6806 | 27.6339 | 198.0467 | 162.5394 | 0 | 1.8438 | 2.4756 | 166.8588 | 31.1879 | 4.2562 | 26.9317 | 35.5074 | 136 | 3401 | 110 | 2127088.24 | 12.19 | 2421.99 | 50.0233 | 51883.37 | 65228.31 | VPC | 17.93% | 5.998% | 3.4287 | N/A | 542.5403 | 26.9317 | 0.53838 | 64.5294 | Water imported | Customer metering inaccuracies | Customer retail unit cost (applied to Apparent Losses) | n/a |  | 7 | 4 | 8 | 8 | 9 | n/a | 7 | 7 | 5 | 8 | 5 | 7 | 9 | 10 | 3 | 9 | 10 | 10 |  | Pickens County Worksheet 2015.xls | 5
Polk County Water Authority | GA2330001 | POLK | 23325 | 860.337 | 4.841 | 23.04 | 842.138 | 522.252 | 0 | 0 | 10.5267 | 532.7787 | 309.3593 | 14.0692 | 295.2901 | 319.886 | 500 | 10700 | 80 | 4117946.9 | 6.88 | 539.8 | 125.852 | 96795.95 | 159397.59 | VPC | 37.98% | 6.359% | 3.6024 | N/A | 1618.0279 | 295.2901 | 2.3463 | 63.205 | Volume from own sources | Customer metering inaccuracies | Variable production cost (applied to Real Losses) | 5 | 5 | 3 | 1 | 3 | 1 | 7 | n/a | n/a | 5 | 5 | 8 | 5 | 5 | 7 | 10 | 4 | 10 | 6 | 5 | QWLA: Tal Woodall -- This audit and the supporting documents were verified with Water Superintendent Ryan Prince. All of the preformance indicators are with in there expected ranges, however; these figures are suspect due to the lack of metere testing and the estimation of the error adjustment. The ILI and Apparent Losses were both on the low end of their range and the Real Losses were in the mid level of the expected range. | Polk County Water Audit 2015.xls | 5
Pooler | GA0510001 | CHATHAM | 21187 | 455.571 | 339.363 | 37.433 | 792.6868 | 688.297 | 0 | 23.231 | 9.9086 | 721.4366 | 71.2503 | 21.9468 | 49.3035 | 104.3898 | 106.5 | 8099 | 61 | 1531267 | 8.07 | 567.06 | 39.8769 | 177110.41 | 27958.04 | VPC | 13.17% | 14.62% | 7.4241 | 16.6784 | N/A | 49.3035 | 1.2364 | 65.9649 | Billed metered | Variable production cost (applied to Real Losses) | Customer metering inaccuracies | 8 | 9 | 7 | 9 | 2 | 3 | 4 | n/a | 10 | 5 | 5 | 4 | 5 | 7 | 9 | 10 | 7 | 10 | 8 | 2 |  | Pooler, City of Worksheet 2015.xls | 5
Port Wentworth | GA0510002 | CHATHAM | 5500 | 73.217 | 259.865 | 0 | 337.0393 | 278.488 | 0 | 0.383 | 4.213 | 283.084 | 53.9553 | 6.506 | 47.4494 | 58.5513 | 53.5 | 3672 | 62 | 842421 | 2.11 | 1615.75 | 19.0145 | 18351.17 | 76666.3 | VPC | 17.37% | 12.16% | 4.8542 | 35.4026 | N/A | 47.4494 | 2.4954 | 50.0955 | Water imported | Volume from own sources | Customer metering inaccuracies | 5 | 1 | 9 | 4 | n/a |  | 8 | n/a | 8 | 2 | 5 | 4 | 5 | 5 | 7 | 10 | 3 | 10 | 4 | 5 | [CRUC converted: $/100 cubic feet (ccf) to $/1000 gallons (US)] | Port Wentworth 2015 Water Audit.xls | 5
Powder Springs | GA0670006 | COBB | 14000 | 0 | 489.362 | 0 | 485.9603 | 406.401 | Note 1 | 0.631 | 6.0745 | 413.1065 | 72.8538 | 10.5377 | 62.3161 | 79.5593 | 97 | 7281 | 110 | 2965864.76 | 6.14 | 2790 | 64.9193 | 64701.35 | 382620.83 | CRUC | 16.37% | 16.47% | 3.9652 | 23.4486 | N/A | 62.3161 | 0.9599 | 75.6282 | Customer metering inaccuracies | Water imported | Billed metered | n/a | n/a | 9 | 5 | n/a | n/a | 7 | n/a | 10 | 5 | 5 | 2 | 5 | 2 | 4 | 10 | 5 | 9 | 8 | 9 | QWLA - Based upon the data now available the ILI is very low but reviewed the production and sales report and the numbers show very little discrepancy. The recommendations made should help address some of the unknowns that are influencing the low ILI | Powder Springs 2015 Water Audit.xls | 5
Quitman | GA0270002 | BROOKS | 4942 | 242.208 | 0 | 0 | 237.4588 | 183 | 0 | 0 | 2.9682 | 185.9682 | 51.4906 | 16.9642 | 34.5264 | 54.4588 | 50 | 2750 | 56 | 906825 | 1.2 | 199.7 | 13.9605 | 20357.03 | 6894.92 | VPC | 22.93% | 3.071% | 16.9008 | 34.3974 | N/A | 34.5264 | 2.4731 | 43.981 | Volume from own sources | Billed metered | Customer metering inaccuracies | 2 | 2 | n/a |  | n/a |  | 3 | n/a | n/a | 5 | 5 | 1 | 5 | 4 | 5 | 10 | 1 | 5 | 4 | 2 | Bill Powell, QWLA # 0030. Working with John Thursby, water superintendent. No Master meter in working condition water is estimated using run time and a time meter. Meters will be upgraded as soon as January 2016 | Quitman City of Worksheet 2015 - (edited version).xls | 5
Reynolds Water System | GA1330046 | GREENE | 6851 | 391.347 | 0 | 0 | 386.5156 | 259.015 | 0 | 1.6 | 4.8314 | 265.4464 | 121.0691 | 12.4728 | 108.5963 | 127.5006 | 154.2 | 3298 | 75.4 | 1147444.5 | 11.4 | 615.98 | 36.5733 | 142189.75 | 66892.82 | VPC | 32.99% | 18.57% | 10.3614 | N/A | 1929.4694 | 108.5963 | 2.9693 | 62.488 | Volume from own sources | Customer metering inaccuracies | Billed metered | 5 | 2 |  |  |  |  | 7 | n/a | 6 | 5 | 5 | 4 | 5 | 7 | 7 | 10 | 7 | 10 | 8 | 9 |  | Reynolds 2015 Water Audit.xls | 5
Richmond Hill | GA0290000 | BRYAN | 12594 | 505.622 | 0 | 0 | 532.1777 | 480.381 | 0 | 1.221 | 6.6522 | 488.2542 | 43.9234 | 7.3961 | 36.5274 | 51.7967 | 90 | 6501 | 52 | 223394 | 4 | 419.77 | 27.7497 | 29584.25 | 15333.1 | VPC | 9.733% | 21.59% | 3.1169 | 15.3938 | N/A | 36.5274 | 1.3163 | 68.5509 | Volume from own sources | Unbilled metered | Customer metering inaccuracies | 8 | 2 | n/a |  | n/a |  | 7 | n/a | 3 | 5 | 5 | 4 | 5 | 9 | 6 | 10 | 8 | 10 | 8 | 7 | Prepared by Charles Heino- QWLA # 0055, Project Manager for Enviroworx Opertations Management- Public Works Provider for the City of Richmond Hill, GA | Richmond Hill, City of Worksheet 2015.xls | 5
Rincon | GA1030001 | EFFINGHAM | 9880 | 316.49 | 0.1044 | 0 | 316.5944 | 303.587 | 0 | 2.773 | 3.9574 | 310.3174 | 6.277 | 2.3183 | 3.9587 | 13.0074 | 1380 | 4793 | 65 | 814970 | 3.5 | 491.78 | 194.6678 | 8113.96 | 1946.81 | VPC | 4.109% | 1.641% | 1.3251 | N/A | 7.8592 | 3.9587 | 0.020336 | 68.5294 | Volume from own sources | Variable production cost (applied to Real Losses) | Customer retail unit cost (applied to Apparent Losses) | 8 | 5 | 8 |  | n/a |  | 7 | n/a | 7 | 5 | 5 | 7 | 5 | 7 | 6 | 4 | 8 | 10 | 5 | 3 |  | Rincon, City of Worksheet 2015.xls | 5
Ringgold | GA0470002 | CATOOSA | 2743 | 127.52 | 33 | 0 | 158.6104 | 135.847 | 0 | 12.414 | 1.9826 | 150.2436 | 8.3667 | 0.88455 | 7.4822 | 22.7634 | 28 | 1261 | 99.8 | 459852 | 4.67 | 337.69 | Note 3 | 4130.86 | 34941.8 | CRUC | 14.35% | 23.12% | 1.9218 | 16.2563 | N/A | 7.4822 | Note 3 | 64.262 | Volume from own sources | Unbilled metered | Water imported | 6 | 3 | 5 | 3 | n/a |  | 7 | n/a | 5 | 5 | 5 | 7 | 5 | 8 | 8 | 10 | 3 | 8 | 8 | 8 | QWLA SPENT A GOOD AMOUNT OF TIMES VERIFYING ALL THE ANSWERS ON THIS REPORT. INFORMATION IS ALL IN A FOLDER MARKED 2015 WATER LOSS AUDIT AND STORED IN WATER BILLER'S OFFICE. THE ONLINE REPORT IS STORED ON THE F:\DRIVE UNDER WATER LOSS REPORTS. | Ringgold, City of Worksheet 2015.xls | 5
Rockdale County Water Resources | GA2470000 | ROCKDALE | 72621 | 4237.5 | 2.972 | 0 | 4283.3051 | 2915.621 | 0 | 42.458 | 53.5413 | 3011.6203 | 1271.6847 | 47.8769 | 1223.8078 | 1367.6841 | 648.84 | 28129 | 100 | 6235452 | 4.07 | 700 | 282.1295 | 194858.99 | 4980897.89 | CRUC | 31.93% | 89.27% | 4.6631 | 119.1972 | N/A | 1223.8078 | 4.3378 | 63.0992 | Volume from own sources | Customer retail unit cost (applied to Apparent Losses) | Variable production cost (applied to Real Losses) | 7 | 3 | 4 | 3 | n/a |  | 7 | 7 | 7 | 5 | 5 | 6 | 5 | 5 | 5 | 10 | 3 | 7 | 5 | 5 | This worksheet is now used as central tool for the water management and accountability team. | Rockdale 2015 Water Audit.xls | 5
Rockmart | GA2330002 | POLK | 6500 | 543.87 | 0 | 0 | 543.87 | 390.479 | 0 | 9.802 | 0.2676 | 400.5486 | 143.3214 | 14.7157 | 128.6057 | 153.391 | 67.5 | 3077 | 60 | 1445279 | 5.33 | 263.37 | 18.1053 | 78434.67 | 33870.88 | VPC | 28.2% | 7.954% | 13.1027 | 114.5091 | N/A | 128.6057 | 7.1032 | 39.5588 | Volume from own sources | Unbilled metered | Customer metering inaccuracies | 3 | 2 | n/a |  | n/a |  | 5 | n/a | 1 | 8 | 5 | 3 | 5 | 3 | 5 | 10 | 2 | 4 | 9 | 3 | QWLA 0071: Spencer Senerman. Brent Edwards is the Public Works Director for the City of Rockmart. Pam Herring is the City Clerk/Finance Officer for the City of Rockmart. Todd Queen is the Fire Chief for the City of Rockmart. Eddie Mitchell is an operator at the water treatment plant for the City of Rockmart. Rockmart should test and calibrate its finished water production meter at the water plant on an annual basis. The City should also consider testing 30 random customer meters for accuracy each year. The results of the testing should be incorporated into next year's audit. Several additional recommendations have been made in the comments section below. It should be noted that apparent losses increased in 2015 when compared to previous year's audits. This is due to an increase in the estimated customer meter inaccuracy. Additionally, the unbilled metered volume in 2015 is significantly less than the 2014 volume; however Pam Herring believes the 2014 volume to be significantly overstated, possibly due to a meter reading or data handling error. It is also worth noting that the 2014 audit was not validated, so a direct comparison of the 2015 audit to the 2014 audit will likely yield inaccurate annual trends. Finally, the total annual cost to operate the water system is trending down, which is unlikely. The estimation of the total annual cost to operate the water system is likely responsible for this trend. | Rockmart, City of Worksheet 2015.xls | 5
Rome | GA1150002 | FLOYD | 45586 | 2487 | 0 | 219 | 2268 | 1720 | 2.4 | 155 | 50.1 | 1927.5 | 340.5 | 113.3 | 227.2 | 545.6 | 287 | 20186 | 85 | 5614570 | 2.6 | 315.45 | 142.1122 | 393796.18 | 71670.24 | VPC | 24.06% | 9.443% | 15.3775 | 30.8365 | N/A | 227.2 | 1.5987 | 74.1053 | Volume from own sources | Variable production cost (applied to Real Losses) | Billed metered | 7 |  | n/a |  | 5 |  | 7 | 9 | 8 | 8 | 7 | 8 | 5 | 8 | 8 | 10 | 6 | 8 | 8 | 5 | [CRUC converted: $/100 cubic feet (ccf) to $/1000 gallons (US)] | Rome, City of Worksheet 2015.xls | 5
Roswell | GA1210009 | FULTON | 14300 | 456.9 | 131.7 | 0 | 588.4816 | 528.1 | 0 | 12 | 7.356 | 547.456 | 41.0256 | 20.0702 | 20.9554 | 60.3816 | 85.1 | 5492 | 88.5 | 3900520 | 7.49 | 1287.56 | 41.4826 | 150325.76 | 26981.29 | VPC | 10.26% | 5.185% | 10.0122 | 10.4537 | N/A | 20.9554 | 0.50516 | 76.0306 | Water imported | Customer retail unit cost (applied to Apparent Losses) | Customer metering inaccuracies | 6 | 8 | 5 | 3 | n/a |  | 9 | n/a | 8 | 8 | 5 | 6 | 9 | 8 | 9 | 10 | 8 | 10 | 9 | 8 | QWLA: Chris Boyd Review Date 3/1/2016 The City of Roswell is in the process of operating a new water treatment plant in 2016. Construction on the new plant began in 2014. In October of 2015, the old plant was shut down and the City began purchasing water from Fulton County while supplementing some of its demand through its well site. During the plant's construction water was utilized by the contractors. In reviewing the Perfomance INdicators it was noticed that the Real Losses were low which directly affected the Real Loss per service connection per day and the ILI. This can be attributed to the City's active Leak Detection Program, the meter testing program, and line replacement program. In 2011, the City implemented its Sensus FlexNet AMI system and replaced 3,500 meters with the new Sensus IPERL smart meter. | Roswell 2015 Water Audit.xls | 5
Sandersville | GA3030005 | WASHINGTON | 7904 | 663.5532 | 0 | 78.6637 | 584.8895 | 387.8623 | 0 | 0 | 7.3111 | 395.1734 | 189.7161 | 3.404 | 186.3121 | 197.0272 | 70.3 | 3066 | 65.5 | 1746946.99 | 2.9 | 92.67 | 20.0876 | 9871.5 | 17265.54 | VPC | 33.69% | 1.592% | 3.0417 | 166.4854 | N/A | 186.3121 | 9.275 | 58.5222 | Volume from own sources | Customer metering inaccuracies | Customer retail unit cost (applied to Apparent Losses) | 3 | 6 | n/a |  | 5 | 1 | 7 | n/a | n/a | 5 | 5 | 5 | 5 | 9 | 7 | 10 | 4 | 10 | 6 | 7 | QWLA: Tal Woodall - All supporting documents and inputs were dicussed and verified with Water Superintendent Seaborn Street. The performance indicators are supported by the age of the infrastructure and water loss control practices. The Apparent Losses, Real Losses and ILI all reported mid levels in their expected ranges. The city produces and supplies power to some of its facilities which resulted in a low Variable production Cost. It is recommended to have all production and export meters tested and recorded annualy. | Sandersville 2015 WATER LOSS AUDIT.xls | 5
Satilla Regional Water & Sewer Authority | GA2990001 | WARE | 10657 | 379.901 | 0 | 0 | 399.8958 | 362.199 | 0 | 0 | 4.9987 | 367.1977 | 32.6981 | 3.7253 | 28.9728 | 37.6968 | 234.5 | 6563 | 51 | 1390463 | 2.8 | 220.47 | 41.9414 | 10430.93 | 6387.62 | VPC | 9.427% | 1.289% | 1.5551 | N/A | 338.4965 | 28.9728 | 0.69079 | 64.3111 | Volume from own sources | Customer metering inaccuracies | Customer retail unit cost (applied to Apparent Losses) | 6 | 5 | n/a | 3 | n/a |  | 7 | n/a | n/a | 5 | 5 | 5 | 5 | 9 | 10 | 10 | 3 | 10 | 5 | 8 | Water Audit completed by: Henry McLaughlin of the Satilla Regional Water and Sewer Authority, Audited by: Will Corbitt QWLA 0022 | Satilla 2015 Water Audit.xls | 5
Savannah - Georgetown Gateway | GA0510081 | CHATHAM | 13504 | 702.9115 | 0 | 0 | 672.6426 | 543.3895 | 0 | 9.6454 | 8.408 | 561.4429 | 111.1997 | 32.1472 | 79.0525 | 129.2531 | 131 | 5772 | 53.5 | 1505319.01 | 1.68 | 184.17 | 30.7462 | 72197.2 | 14559.1 | VPC | 19.22% | 5.984% | 15.2589 | 37.5229 | N/A | 79.0525 | 2.5711 | 52.6299 | Volume from own sources | Billed metered | Customer metering inaccuracies | 5 | 3 | n/a |  | n/a |  | 5 | n/a | 5 | 5 | 5 | 4 | 5 | 7 | 5 | 10 | 9 | 8 | 6 | 4 | [CRUC converted: $/100 cubic feet (ccf) to $/1000 gallons (US)] | Savannah Georgetown Worksheet 2015.xls | 5
Savannah - Savannah Main | GA0510003 | CHATHAM | 16858 | 6425.5591 | 0 | 26.8326 | 7034.2214 | 5738.8403 | 0 | 123.9762 | 87.9278 | 5950.7442 | 1083.4771 | 340.5019 | 742.9752 | 1295.3811 | 690 | 56102 | 61.1 | 11229946 | 1.21 | 170.78 | 270.9231 | 412007.35 | 126885.3 | VPC | 18.42% | 5.121% | 16.6283 | 36.283 | N/A | 742.9752 | 2.7424 | 53.1203 | Volume from own sources | Billed metered | Customer metering inaccuracies | 5 | 3 | n/a |  | 5 | 3 | 5 | n/a | 5 | 5 | 5 | 4 | 5 | 7 | 5 | 10 | 9 | 8 | 6 | 4 |  | Savannah Main Worksheet2015.xls | 5
Savannah - Savannah Quarters | GA0510259 | CHATHAM | 3530 | 120.6026 | 0 | 4.0043 | 111.4049 | 98.321 | 0 | 0.672 | 1.3926 | 100.3856 | 11.0193 | 2.5446 | 8.4747 | 13.0839 | 23 | 1048 | 53.7 | 261787.95 | 1.74 | 274.52 | Note 3 | 5918.8 | 2326.48 | VPC | 11.74% | 3.366% | 6.6521 | 22.155 | N/A | 8.4747 | Note 3 | 53.9822 | Volume from own sources | Customer metering inaccuracies | Variable production cost (applied to Real Losses) | 5 | 3 | n/a |  | 8 | 4 | 6 | n/a | 5 | 5 | 5 | 3 | 5 | 7 | 5 | 10 | 10 | 8 | 5 | 4 |  | Savannah Quarters Worksheet 2015.xls | 5
Savannah - Whitemarsh | GA0510250 | CHATHAM | 4215 | 275.0596 | 0 | 0 | 263.2149 | 209.4329 | 0 | 0.089766 | 3.2902 | 212.8128 | 50.4021 | 12.2091 | 38.1929 | 53.782 | 24.3 | 1661 | 62.9 | 453310.4 | 1.52 | 171.74 | Note 3 | 24808.27 | 6559.26 | VPC | 20.43% | 7.048% | 20.1383 | 62.9971 | N/A | 38.1929 | Note 3 | 53.3946 | Volume from own sources | Billed metered | Customer metering inaccuracies | 5 | 2 | n/a |  | n/a |  | 5 | n/a | 6 | 5 | 5 | 4 | 5 | 7 | 5 | 10 | 9 | 8 | 6 | 4 | [CRUC converted: $/100 cubic feet (ccf) to $/1000 gallons (US)] | Savannah Whitemarsh Worksheet 2015.xls | 5
Savannah - Wilmington | GA0510229 | CHATHAM | 13652 | 493.013 | 0 | 0 | 471.7828 | 403.0003 | 0 | 0 | 5.8973 | 408.8976 | 62.8852 | 23.3975 | 39.4877 | 68.7825 | 57 | 5200 | 55.7 | 878091.91 | 1.58 | 138.67 | 22.1271 | 49419.09 | 5475.76 | VPC | 14.58% | 6.345% | 12.3274 | 20.8049 | N/A | 39.4877 | 1.7846 | 52.8763 | Volume from own sources | Billed metered | Customer metering inaccuracies | 5 | 3 | n/a |  | n/a |  | 5 | n/a | n/a | 5 | 5 | 6 | 5 | 6 | 6 | 10 | 10 | 5 | 6 | 4 | [CRUC converted: $/100 cubic feet (ccf) to $/1000 gallons (US)] | Savannah Wilmington Worksheet 2015.xls | 5
Senoia | GA0770003 | COWETA | 4589 | 144.877 | 2.909 | 0 | 147.786 | 131.38 | 0.529 | 0.053 | 1.8473 | 133.8093 | 13.9767 | 7.6154 | 6.3612 | 15.877 | 45 | 1965 | 70 | 863400 | 1 | 91 | 13.751 | 7615.44 | 578.87 | VPC | 10.74% | 0.9691% | 10.6179 | 8.8692 | N/A | 6.3612 | 0.4626 | 49.1543 | Volume from own sources | Billed unmetered | Billed metered | 5 | 4 | 1 | 1 | n/a | n/a | 5 | n/a | 7 | 5 | 5 | 4 | 5 | 1 | 3 | 10 | 1 | 7 | 5 | 5 | Prepared by: Lynn Carter | Senoia 2015 Water Audit.xls | 5
Smyrna | GA0670007 | COBB | 35000 | 0 | 1540.985 | 0 | 1541.7559 | 1321.799 | 0 | 48.454 | 19.2719 | 1389.5249 | 152.2309 | 19.1847 | 133.0462 | 219.9569 | 200.5 | 15294 | 106 | 11635399 | 4.96 | 2955.7 | 130.726 | 95156.18 | 393244.7 | VPC | 14.27% | 5.918% | 3.4367 | 23.8335 | N/A | 133.0462 | 1.0177 | 78.7721 | Water imported | Customer metering inaccuracies | Unauthorized consumption | n/a |  | 9 | 2 | n/a |  | 8 | n/a | 7 | 5 | 5 | 6 | 5 | 5 | 5 | 10 | 2 | 9 | 8 | 10 | The City of Smyrna is a medium size water utility. Smyrna is located about 10 miles northwest of Atlanta, Georgia and is considered an integral part of the Metro Atlanta area. More than 50,000 residents call Smyrna home, and this area of Cobb County continues to be attractive for residential development. In 2005 there was a major changeout of the residential meter infrastructure with 100% now being Master Meter brand AMR meters. Since that time the majority of the larger meters have also been changed to new AMR meters or retrofitted with AMR technology. In March of 2015 there was a billing software upgrade and several of the conversion issues and nuances of the new software have been worked out throughout the year. Auditor: Kieran Dozeman - Utility Billing Coordinator QWLA: Kieran Dozeman #0120 - Audited 3/2/2106 | Smyrna 2015 Water Audit.xls | 5
Social Circle | GA2970002 | WALTON | 4235 | 214.71 | 17.01 | 0 | 225.4663 | 166.14 | 0 | 0 | 2.8183 | 168.9583 | 56.508 | 1.3954 | 55.1126 | 59.3263 | 24 | 1800 | 65 | 975853 | 9.85 | 0.01 | Note 3 | 13744.76 | 542858.86 | CRUC | 26.31% | 59.88% | 2.1239 | 83.8852 | N/A | 55.1126 | Note 3 | 55.3718 | Volume from own sources | Billed metered | Customer metering inaccuracies | 4 | 2 | 4 | 2 | n/a | n/a | 6 | 5 | n/a | 8 | 5 | 5 | 5 | 6 | 6 | 10 | 5 | 9 | 7 | 7 | QWLA :AUTRON HAYES 0063 | Social Circle, City of Worksheet 2015.xls | 5
South Monroe County Water System | GA2070074 | MONROE | 5370 | 0 | 229.08 | 0 | 238.625 | 172.802 | 0 | 33.886 | 0.247 | 206.935 | 31.69 | 1.0286 | 30.6614 | 65.823 | 69 | 4516 | 76 | 1685000 | 4.15 | 3500 | 29.1461 | 4268.56 | 107315.01 | VPC | 27.58% | 13.71% | 0.624 | 18.6014 | N/A | 30.6614 | 1.052 | 67.0713 | Water imported | Customer metering inaccuracies | Billed metered
Spalding County Water and Sewerage Facilities Authority | GA2550036 | SPALDING | 40430 | 0 | 1190.577 | 0 | 1190.577 | 775.941 | 0 | 27.408 | 14.8822 | 818.2312 | 372.3458 | 17.15 | 355.1958 | 414.636 | 495.5 | 14861 | 103 | 1099029 | 8.51 | Note 2 & B | 207.5987 | 145946.81 | Note 4 | VPC | 34.83% | 13.28% | 3.1617 | N/A | 1963.9537 | 355.1958 | 1.711 | 52.4412 | Water imported | Unauthorized consumption | Systematic data handling errors | n/a |  | 1 |  | n/a |  | 8 | n/a | 7 | 5 | 5 | 7 | 5 | 9 | 9 | 1 | 3 | 10 | 8 | 10 | SCWSA has worked with the City of Griffin this past year to define areas of improvement in both water loss as well as reporting information with more detail. SCWSA will continue to attempt to identify area of improvement in the reporting and water loss area in the coming year. | Spalding Co 2015 Water Audit.xls | 5
Sparta | GA1410001 | HANCOCK | 3710 | 279.08 | 0 | 35.988 | 237.1109 | 137.72 | 0 | 3.25 | 2.9639 | 143.9339 | 93.1771 | 16.583 | 76.5941 | 99.3909 | 53 | 2029 | 59 | 1082525 | 3.29 | 1029.4 | 12.7289 | 54558.1 | 78845.92 | VPC | 41.92% | 12.91% | 22.3918 | 103.4237 | N/A | 76.5941 | 6.0173 | 47.8743 | Volume from own sources | Customer metering inaccuracies | Billed metered | 1 | 8 | n/a |  | 8 | 8 | 4 | n/a | n/a | 5 | 5 | 1 | 5 | 6 | 5 | 10 | 9 | 10 | 8 | 9 | Bill Powell QWLA # 00030 met with William Evans, Mayor, Virginia Brown, City Manager, James T. Griffin, Water Superintendent and Myristine Colbert, Utilities Supervisor. Because there is a state prison being served by the city, each inmate is counted in the population to determine the requirement for completing the water audit. Therefore, using EPD's calculation of 2.6 people per connection generates an additional 488 connections. All other connections are treated as one (1) connection. | Sparta, City of Worksheet 2015 ( 07-26-2016).xls | 5
St. Marys Water Dept. | GA0390001 | CAMDEN | 29402 | 532.706 | 0 | 0 | 517.1903 | 430.557 | Note 1 | 1.33 | 8.533 | 440.42 | 76.7703 | 22.7201 | 54.0502 | 86.6333 | 130 | 6903 | 53 | 1453435 | 2.86 | 254.17 | 33.6361 | 64979.38 | 154583.65 | CRUC | 16.75% | 17.05% | 9.0173 | 21.452 | N/A | 54.0502 | 1.6069 | 75.5216 | Customer retail unit cost (applied to Apparent Losses) | Variable production cost (applied to Real Losses) | Volume from own sources | 7 | 5 | n/a |  | n/a |  | 6 | n/a | 9 | 8 | 5 | 4 | 5 | 7 | 7 | 10 | 8 | 10 | 5 | 7 | Comments made by Brian Gaddy QWALA. | St Marys 2015 water audit.xls | 5
Statesboro | GA0310004 | BULLOCH | 36846 | 1184.338 | 0 | 0 | 1223.4897 | 1163.051 | Note 1 | Note 1 | 15.2936 | 1178.3446 | 45.145 | 23.6778 | 21.4673 | 60.4387 | 240 | 14438 | 62.3 | 2015086 | 4.62 | 270.53 | 78.7719 | 109391.38 | 5807.54 | VPC | 4.94% | 5.922% | 4.493 | 4.0736 | N/A | 21.4673 | 0.27252 | 50.1078 | Volume from own sources | Billed metered | Variable production cost (applied to Real Losses) | 5 | 2 | n/a |  | n/a |  | 7 | n/a | n/a | 5 | 5 | 5 | 5 | 5 | 7 | 10 | 4 | 5 | 5 | 4 | QWLA: Tal Woodall -- The information for this audit was provided and verified by Danny Lively. The performance indicators all reported low and are supported by the loss control practices conducted by the utility. Ongoing meter replacement and testing, as well as, planned software and technology upgrades will further support loss control efforts. | Statesboro, City of Worksheet 2015.xls | 5
Statham | GA0130001 | BARROW | 3976 | 85.13 | 25.92 | 0 | 109.3336 | 91.141 | 0 | 2.639 | 1.3667 | 95.1467 | 14.1869 | 3.4016 | 10.7853 | 18.1926 | 38 | 1755 | 83 | 658246 | 6.39 | 921 | Note 3 | 21736.22 | 9933.3 | VPC | 16.64% | 5.372% | 5.3102 | 16.837 | N/A | 10.7853 | Note 3 | 50.4953 | Volume from own sources | Unbilled metered | Customer metering inaccuracies
Stockbridge Water | GA1510004 | HENRY | 6500 | 145.776 | 96.5958 | 0 | 248.0414 | 201.403 | 0 | 8.256 | 3.1005 | 212.7595 | 35.2819 | 0.60077 | 34.6812 | 46.6384 | 47 | 2764 | 88.63 | 1971262.56 | 6.67 | 413.95 | 21.6379 | 4007.14 | 14356.27 | VPC | 18.8% | 1.17% | 0.59549 | 34.3766 | N/A | 34.6812 | 1.6028 | 63.5649 | Volume from own sources | Unbilled metered | Customer metering inaccuracies | 5 | 3 | 9 | 3 | n/a |  | 7 | n/a | 1 | 4 | 5 | 3 | 5 | 5 | 9 | 10 | 3 | 9 | 9 | 10 | qulified water loss auditor(qwla)- chad hitzeman #0104. scada computer was taken out of service during this audit year. A new, updated system is in the works for 2016. meter replacement and automatic wireless reading system to be implamented in 2016. recomend a more through system of accountability for hydrant flushing, leak detction, and estimation of water loss from emergency leaks. | Stockbridge 2015 Water Audit.xls | 5
Summerville | GA0550003 | CHATTOOGA | 11651 | 712.36 | 0 | 31.312 | 657.4213 | 534.66 | Note 1 | Note 1 | 8.2178 | 542.8778 | 114.5435 | 31.1202 | 83.4233 | 122.7613 | 225 | 5168 | 80 | 1206527.76 | 5.91 | 287.31 | 58.1795 | 183920.4 | 493031.71 | CRUC | 18.67% | 60.13% | 16.4978 | N/A | 1015.8088 | 83.4233 | 1.4339 | 56.2831 | Volume from own sources | Variable production cost (applied to Real Losses) | Unauthorized consumption | 3 | 3 | n/a |  | 3 | 3 | 9 | 5 | n/a | 5 | 5 | 9 | 5 | 3 | 6 | 10 | 3 | 10 | 7 | 3 |  | Summerville 2015 WATER AUDIT.xls | 5
Swainsboro | GA1070005 | EMANUEL | 8500 | 411.456 | 0 | 0 | 417.7218 | 257.148 | 0 | 3.898 | 5.2215 | 266.2675 | 151.4543 | 9.7608 | 141.6935 | 160.5738 | 60 | 3093 | 55 | 939430.36 | 2.48 | 327.29 | 15.8301 | 24206.69 | 46374.88 | VPC | 38.44% | 7.831% | 8.6459 | 125.5097 | N/A | 141.6935 | 8.9509 | 68.7431 | Billed metered | Customer metering inaccuracies | Unbilled metered | 5 | 2 | n/a |  | n/a |  | 7 | n/a | 5 | 5 | 5 | 3 | 5 | 6 | 7 | 10 | 8 | 6 | 6 | 5 | QWLA: Tal Woodall -- All data was provided and verified with Johnny Mills, Collection and Distribution Supervisor. All performance indicators reported low on their expected ranges. This is suspected to be due to the lack of source meter testing results. It was provided that all source meters are approxamately 10 years old and were found to be under-registering by the last meter test. It is advised to have all soucre meters tested and calibrated or replaced as needed. It is also recommended to review and update the rate structure as needed. | Swainsboro, City of Worksheet 2015.xls | 5
Sylvester | GA3210003 | WORTH | 6443 | 347.579 | 0 | 0 | 340.7637 | 243.379 | Note 1 | 3.8771 | 4.2595 | 251.5156 | 89.2481 | 14.4738 | 74.7742 | 97.3847 | 80.5 | 3070 | 80 | 483240.08 | 2.13 | 202.23 | 26.1633 | 30829.27 | 15121.6 | VPC | 28.58% | 9.849% | 12.9167 | 66.7299 | N/A | 74.7742 | 2.858 | 62.3333 | Volume from own sources | Customer metering inaccuracies | Billed metered | 6 | 3 |  |  |  |  | 5 |  |  | 5 | 5 | 1 | 5 | 1 | 4 | 10 | 1 | 9 | 8 | 6 |  | Sylvester 2015 water audit.xls | 5
Talbot County Water Works | GA2630005 | TALBOT | 3398 | 0 | 133.367 | 41.24 | 92.127 | 71.609 | 0 | 2.539 | 1.1516 | 75.2996 | 16.8274 | 1.5385 | 15.2889 | 20.518 | 150 | 1641 | 70 | 1150975.64 | 4.5 | 2537.85 | 27.023 | 6923.24 | 38800.97 | VPC | 22.27% | 4.786% | 2.5686 | N/A | 279.2496 | 15.2889 | 0.56578 | 52.8075 | Water imported | Water exported | Customer metering inaccuracies | n/a |  | 5 | 1 | 3 | 1 | 7 | n/a | 5 | 5 | 5 | 3 | 5 | 3 | 7 | 10 | 1 | 10 | 6 | 5 | QWLA: Tal Woodall -- All components of this audit were provided and verified by Supervisor Alicia Neals. The Apparent Losses reported low and Real losses reported high indicating there might be an under estimation of the Apparent losses. This is most likely due to the lack of export and customer meter testing. This may also be a representative of an inaccurate average operating pressure. It is recommended to test the export meters and have them calibrated or replaced as needed. It is also recommended to begin a customer meter testing program, as well as, system pressure monitoring. | Talbot County Water Worksheet 2015.xls | 5
Tallapoosa | GA1430002 | HARALSON | 4030 | 0 | 195.06 | 0 | 192.8233 | 152.701 | 0 | 0 | 2.4103 | 155.1113 | 37.712 | 3.9802 | 33.7318 | 40.1223 | 31 | 1721 | 80 | 903929.94 | 5.02 | 2610 | Note 3 | 19972.43 | 88040 | VPC | 20.81% | 12.65% | 6.3362 | 53.699 | N/A | 33.7318 | Note 3 | 78.3413 | Customer metering inaccuracies | Customer retail unit cost (applied to Apparent Losses) | Unauthorized consumption | n/a | n/a | 10 | 3 | n/a |  | 6 | n/a | n/a | 5 | 5 | 2 | 5 | 5 | 7 | 10 | 3 | 10 | 5 | 10 | By, Rickey Hicks, Haralson County Water Plant Supervisor and QWLA: The City of Tallapoosa imports all of its water from Haralson County Water Authority. I talked with Natalie Wade over the phone and reviewed the previous notes by Cavanaugh, taken during their Validation process. I also had copies of Haralson County Water's records since I Did their audit and validation, which helped with the water imported section. | Tallapoosa, City of Worksheet 2015.xls | 5
Temple | GA0450005 | CARROLL | 4500 | 0 | 130.275 | 0 | 130.275 | 140.914 | Note 1 | 3.146 | 1.6284 | 145.6884 | -15.4134 | 5.9029 | -21.3164 | -10.639 | 44 | 2696 | 50 | 650225 | 4.5 | 2170 | 11.7245 | 26563.26 | -46256.55 | VPC | -8.167% | -1.435% | 5.9987 | -21.6621 | N/A | -21.3164 | -1.8181 | 50.8922 | Water imported | Customer metering inaccuracies | Billed metered | n/a |  | 7 | 2 | n/a |  | 5 | n/a | 6 | 5 | 5 | 2 | 5 | 5 | 5 | 10 | 1 | 4 | 4 | 10 | QWLA - Great concern with extremely low ILI. 100% of water is purchased and metering system has low flow and high flow. QWLA looked at each meter and determined each meters hi, low and avg flow rates to apply an accuracy test adjustments based on calibration. This increased total purchased water by over 6 MG. Although majority of system is less than 25 years old, City has minimal programs and funds to track leaks. I think ILI is out of range but I cannot find enough substantial data to qualify why it is so low. PW Director and I have been discussing meter replacement program and hope to convert all older meters to ARM (approximately 25% of system is ARM now). I spoke with person who prepared audit last year and they found +/- same results. As QWLA for Temple I will request old audits from EPD so PW Director and I can begin evaluating data to scrub and determine if these numbers are authentic. | TEMPLE 2015 Water Audit.xls | 5
The Landings Subdivision | GA0510033 | CHATHAM | 11058 | 531.015 | 0 | 0 | 529.426 | 498.162 | 0 | 0.248 | 1.434 | 499.844 | 29.582 | 10.159 | 19.423 | 31.264 | 95.4 | 4700 | 56.5 | 781288 | 7.93 | 507.43 | 25.1824 | 80560.63 | 154024.63 | CRUC | 5.905% | 31.73% | 5.9219 | 11.3221 | N/A | 19.423 | 0.77129 | 78.9282 | Volume from own sources | Variable production cost (applied to Real Losses) | Unauthorized consumption | 8 | 3 | n/a | n/a | n/a |  | 9 | n/a | 8 | 8 | 5 | 6 | 5 | 8 | 10 | 10 | 8 | 10 | 10 | 5 | QWLA: Ron Medders Registry # 0032- Utility is within a gated very water conscious community which drives the utility owner to operate the system at a high level of service. Progressive conservation and leak detection measures have been adopted since initial groundwater withdrawal reductions were incurred in 2009 to help mitigate salt water intrusion happening in Hilton Head SC. | The Landings 2015 Water Audit.xls | 5
Thomaston | GA2930000 | UPSON | 12482 | 622.11 | 0 | 26.668 | 595.442 | 413.243 | Note 1 | 18.937 | 7.443 | 439.623 | 155.819 | 15.8881 | 139.9309 | 182.199 | 80 | 4801 | 75 | 2409207 | 5.9 | 559.43 | 31.562 | 93739.82 | 78281.53 | VPC | 30.6% | 7.753% | 9.0667 | 79.8526 | N/A | 139.9309 | 4.4335 | 48.1211 | Volume from own sources | Customer metering inaccuracies | Billed metered | 4 | 3 |  |  | 7 | 3 | 5 | 5 | 7 | 5 | 5 | 2 | 5 | 4 | 3 | 1 | 3 | 9 | 7 | 4 |  | Thomaston, City of Worksheet 2015.xls | 5
Thomasville | GA2750005 | THOMAS | 24206 | 1731.017 | 0 | 0 | 1766.3439 | 1347.013 | Note 1 | Note 1 | 22.0793 | 1369.0923 | 397.2516 | 35.2735 | 361.9781 | 419.3309 | 262.5 | 14205 | 66.3 | 4157494 | 3.59 | 248.51 | 85.9294 | 126631.7 | 89955.18 | VPC | 23.74% | 5.342% | 6.8032 | 69.8149 | N/A | 361.9781 | 4.2125 | 71.5889 | Volume from own sources | Customer retail unit cost (applied to Apparent Losses) | Unauthorized consumption | 7 | 5 | n/a |  | n/a |  | 7 | n/a | n/a | 5 | 5 | 6 | 5 | 8 | 7 | 10 | 6 | 10 | 6 | 8 | QWLA : Tal Woodall -- All inputs provided for this audit were verified with Water Superintendent Stacey Thomas. All performance indicators reported within their expected ranges. Real Losses were in the low-to-mid range. Apparent losses were on the low end of the range. The ILI reported in the middle of the range. These results are supported by the utiliies overall water loss controll practices. | Thomasville, City of Worksheet 2015.xls | 5
Thomson - McDuffie County | GA1890001 | MCDUFFIE | 17717 | 741.52 | 0 | 0 | 734.1782 | 582.675 | Note 1 | Note 1 | 21.38 | 604.055 | 130.1232 | 15.1835 | 114.9398 | 151.5032 | 278.5 | 6504 | 62 | 2874145 | 4.21 | 605.06 | 56.1741 | 63922.36 | 69545.06 | VPC | 20.64% | 5.094% | 6.3958 | N/A | 1130.7126 | 114.9398 | 2.0461 | 51.6974 | Volume from own sources | Billed metered | Customer metering inaccuracies | 6 | 4 |  |  |  |  | 3 |  |  | 4 | 5 | 3 | 5 | 6 | 7 | 10 | 2 | 5 | 5 | 5 | Audit perpaired by Charles Cumber. QWLA: David Crawley, 0025 | Thomson-McDuffie Worksheet 2015.xls | 5
Tifton - Tift County Water System | GA2770001 | TIFT | 24871 | 1713.128 | 0 | 0.0072 | 1713.1208 | 1289.643 | 0 | 0 | 21.414 | 1311.057 | 402.0638 | 37.867 | 364.1968 | 423.4778 | 285 | 11643 | 59.9 | 3388000 | 1.44 | 238.16 | 71.8937 | 54528.45 | 86737.11 | VPC | 24.72% | 4.32% | 8.9105 | 85.6995 | N/A | 364.1968 | 5.0658 | 70.8667 | Volume from own sources | Variable production cost (applied to Real Losses) | Unauthorized consumption | 7 | 2 | n/a |  | 7 | 5 | 9 | n/a | n/a | 5 | 5 | 7 | 5 | 4 | 6 | 10 | 2 | 10 | 8 | 5 | QWLA: Overall the volume of water produced and volume of water sold went up from 2014. All performance indicators fall in normal range. The utility could see some improvement in audit by working towards meter accuracy testing in addition to electronic calibration and by beginning a customer meter replacement program as their new meters start to extend past warranty coverage. The city has a water model which could also be utilized in determination of the average system pressure. | Tifton Water Audit 2015 final.xls | 5
Toccoa | GA2570001 | STEPHENS | 24960 | 1205.32 | 0 | 223.655 | 1312.0756 | 703.391 | 0 | 105.824 | 60.12 | 869.335 | 442.7406 | 22.9881 | 419.7524 | 608.6846 | 610 | 10716 | 125 | 4830504 | 5.44 | 361.72 | 223.9047 | 125055.46 | 151832.85 | VPC | 46.39% | 6.975% | 5.8773 | N/A | 1885.2569 | 419.7524 | 1.8747 | 57.8707 | Volume from own sources | Customer metering inaccuracies | Customer retail unit cost (applied to Apparent Losses) | 8 | 3 | n/a | n/a | 7 | 4 | 7 | n/a | 8 | 8 | 5 | 4 | 5 | 4 | 4 | 10 | 4 | 10 | 5 | 5 | QWLA: Alex Wiseman - registration #0066. All mandatory data for audit validation submitted by City. Validation date 02/29/2016. Review of performance indicataors: normalized apparent and real losses within expected ranges, CRUC and VPC within expected ranges, ILI is below acceptable range. Data has been double checked for audit (input) errors with none discovered. City is likely over-reporting volumes leaving the system and/or under-reporting volumes entering distribution system. Since finish water production meter has no accuracy testing this reporting period, it is very likely a higher measuring error is in effect. Additionally, there is at least one large meter with significant error that should also be tested for accuracy. Other potential sources of measuring error include the unbilled metered volume. City should re-evaluate this category and also implement storage volume changes in elevated tanks in daily volume estimates. City should continue to track ILI once additional accuracy testing is completed. | Toccoa 2015 Water Audit.xls | 5
Towns County Water and Sewerage Authority | GA2810007 | TOWNS | 9991 | 0 | 245.98 | 0 | 245.98 | 135.2295 | 0 | 0.02737 | 6.208 | 141.4649 | 104.5151 | 1.519 | 102.9961 | 110.7505 | 204 | 4222 | 100 | 1678616 | 5.12 | 1737.63 | 63.3983 | 7777.4 | 178969.12 | VPC | 45.02% | 11.77% | 0.98572 | N/A | 1383.2408 | 102.9961 | 1.6246 | 67.5784 | Water imported | Billed metered | Customer metering inaccuracies | n/a |  | 5 | 3 | n/a |  | 4 | n/a | 1 | 8 | 5 | 2 | 5 | 7 | 6 | 10 | 1 | 5 | 5 | 10 | QWLA 0071: Spencer Senerman. Jennifer Nichols is the office manager of the Towns County Water and Sewerage Authority. Richard Green is the Authority's Operations manager. For next year, it is recommended the Authority try to use calendar year financial information instead of fiscal year financial information for the Total Annual Cost of Operating Water System. Additionally, this audit indicates the ILI is within acceptable limits; however, given the sprawling nature of the Authority's system and low connection density, it is better to use real losses/mile as an indicator of leakage. Apparent losses are likely greater than indicated. Increased meter accuracy testing will give the Authority a greater understanding of apparent losses. Performance indicators such as real losses, apparent losses/conn/day, real loss/length of main etc. will likely become more accurate with increased customer meter testing. | Towns County 2015 Water Audit.xls | 5
Tybee Island Water & Sewer Dept. | GA0510005 | CHATHAM | 7654 | 286.262 | 0 | 0 | 293.6021 | 252.886 | 0 | 2.641 | 3.67 | 259.197 | 34.405 | 2.6503 | 31.7548 | 40.7161 | 33.9 | 3371 | 55.2 | 813091 | 3.83 | 124.18 | 13.883 | 10150.55 | 3943.3 | VPC | 13.87% | 1.83% | 2.154 | 25.8082 | N/A | 31.7548 | 2.2873 | 71.8852 | Volume from own sources | Variable production cost (applied to Real Losses) | Billed metered | 7 | 7 | n/a |  | n/a |  | 8 | n/a | 8 | 5 | 5 | 8 | 5 | 5 | 5 | 10 | 3 | 5 | 7 | 5 | 2015 WATER LOSS AUDIT AS PERFORMED BY RICKY GOODMAN CITY OF TYBEE ISLAND GA. WITH THE ASSISTENCE OF: GEORGE REESE, WATER & SEWER DEPT. SUPERINTENDENT. NALENE CONWAY: BILLING MANAGER. VARIOUS CITY EMPLOYEES INDICATING UNBILLED/UNMETERED CONSUMPTION. OVERVIEW OF 2012 AND 2013 AUDITS AVAILABLE AS WELL AS 2012, 2013 AND 2014 WATER LOSS AUDITS. | Tybee Island 2015 Water Audit.xls | 5
Unadilla | GA0930003 | DOOLY | 3522 | 215.681 | 0 | 0 | 215.681 | 141.436 | Note 1 | 0.072 | 2.696 | 144.204 | 71.477 | 5.6229 | 65.8541 | 74.245 | 34 | 800 | 55 | 614900 | 4 | 128.41 | Note 3 | 22491.67 | 8456.31 | VPC | 34.42% | 5.091% | 19.2566 | N/A | 5306.5325 | 65.8541 | Note 3 | 50.5686 | Volume from own sources | Variable production cost (applied to Real Losses) | Unbilled metered | 5 | 2 | n/a |  | n/a |  | 4 | n/a | 3 | 5 | 5 | 3 | 4 | 2 | 5 | 10 | 1 | 2 | 5 | 1 |  | Unadilla, City of Worksheet 2015.xls | 4.2
Union City | GA1210010 | FULTON | 18636 | 0 | 486.455 | 0 | 491.3687 | 395.277 | 0 | 61.5979 | 6.1421 | 463.017 | 28.3517 | 11.5406 | 16.8111 | 96.0917 | 72.2 | 4441 | 105.18 | 4278104.05 | 8.68 | 7252.97 | 40.5694 | 100172.34 | 121930.31 | VPC | 19.56% | 16.68% | 7.1196 | 10.371 | N/A | 16.8111 | 0.41438 | 33.3235 | Water imported | Unbilled metered | Total annual cost of operating water system | n/a |  | 4 | 1 | n/a |  | 6 | n/a | 2 | 5 | 5 | 4 | 5 | 6 | 3 | 10 | 2 | 3 | 5 | 6 |  | Union City, City of Worksheet 2015.xls | 5
Upson County Water | GA2930010 | UPSON | 4878 | 133.521 | 2.749 | 0 | 136.27 | 126.138 | 0 | 0.593 | 1.7034 | 128.4344 | 7.8356 | 1.9361 | 5.8995 | 10.132 | 71.4 | 1919 | 82.5 | 1126958.66 | 4.5 | 799.93 | 20.2996 | 8712.59 | 4719.18 | VPC | 7.435% | 1.355% | 2.7642 | N/A | 226.3725 | 5.8995 | 0.29062 | 51.1706 | Volume from own sources | Unbilled metered | Customer metering inaccuracies | 3 | 2 | 9 | 2 |  |  | 7 |  | 10 | 5 | 5 | 4 | 5 | 6 | 7 | 10 | 2 | 10 | 5 | 5 | QWLA: Tal Woodall --- All inputs and supporting documents were reviewed with Water Superintendent, Dwight Smith. The resulting performance indicators are low and/or below the expected range. Based on the data and observations made during the validation process this is most likely the result of an inaccurate Water Supplied Volume due to the lack of production meter testing. It is recommended to have all the the source meters tested for accuracy and calibrated or replaced as needed. | Upson County Worksheet 2015.xls | 5
USA - Fort Stewart - Main | GA1790024 | LIBERTY | 27573 | 633.692 | 0 | 0 | 640.0929 | 292.802 | 158.829 | 2.6 | 100 | 554.231 | 85.8619 | 17.8797 | 67.9822 | 188.4619 | 161.7 | 2677 | 57 | 274855 | 0.44 | 72.71 | 26.5544 | 7867.07 | 4942.99 | VPC | 29.44% | 7.375% | 18.2987 | N/A | 1151.8408 | 67.9822 | 2.5601 | 50.5895 | Volume from own sources | Billed metered | Customer metering inaccuracies | 8 | 3 | n/a | n/a | n/a |  | 1 | 4 | n/a | 3 | 5 | 1 | 5 | 8 | 5 | 10 | 6 | 2 | 6 | 2 | Fort Stewart Main GA1790024. This is a Military Installation. Groundwater is the source of drinking water. Fort Stewart drinking water is supplied by the upper and lower floridan aquifers. The Installation supplies its own water. The water is withdrawn on the Installation and is supplied throughout the water distribution system. Since Fort Stewart is a Military Installation; many facilities are not billed for water. *Retail Cost is the same as Production Cost. QWLA: Brian Skeens, #0000 | USA-Fort Stewart Worksheet (1790024) 2015.xls | 5
USA - Hunter Army Airfield - Main | GA0510107 | CHATHAM | 7500 | 158.0381 | 2.887 | 0 | 162.5506 | 18.047 | 60 | 0 | 50 | 128.047 | 34.5036 | 1.4013 | 33.1023 | 84.5036 | 66.4 | 980 | 55 | 151247 | 0.46 | 129.89 | 10.1624 | 640.41 | 4299.65 | VPC | 51.99% | 7.56% | 3.9176 | N/A | 1365.8306 | 33.1023 | 3.2573 | 48.8601 | Volume from own sources | Billed metered | Customer metering inaccuracies | 8 | 2 | 8 | 3 | n/a |  | 1 | 3 | n/a | 3 | 5 | 1 | 5 | 8 | 5 | 10 | 4 | 2 | 6 | 2 | Hunter Army Airfield (GA0510107). This is a Military Installation. Hunter Army Airfield drinking water is supplied by the upper and lower floridan aquifers. The Installation supplies its own water and purchases water from the City of savannah. Since Hunter Army Airfield is a Military Installation; many facilities are not billed for water. *Retail Cost is the same as Production Cost. QWLA: Brian Skeens, #0000 | USA-Hunter Army Airfield-Main Worksheet (0510107) 2015.xls | 5
USAF - Moody Air Force Base - Main | GA1850125 | LOWNDES | 6500 | 104.838 | 0 | 0 | 104.838 | Note 1 & A | Note 1 | 26.208 | 1.3105 | 27.5185 | 77.3195 | 0.52682 | 76.7927 | 104.838 | 100.2 | 490 | 65 | 277549 | 3.11 | 377.72 | 16.256 | 2190.25 | 29006.14 | VPC | 100% | 14.98% | 2.9456 | N/A | 2099.7102 | 76.7927 | 4.724 | 52.0116 | Volume from own sources | Customer metering inaccuracies | Variable production cost (applied to Real Losses) | 7 | 5 | n/a |  | n/a |  | n/a | n/a | 7 | 5 | 5 | 3 | 1 | 10 | 1 | 4 | 6 | 4 | 5 | 3 | QWLA Brandon Rice 0038 rice.brandon79@yahoo.com 2295396976 [CRUC converted: $/100 cubic feet (ccf) to $/1000 gallons (US)] | USAF-Moody AB Main Worksheet 2015.xls | 5
USMC - Marine Corps Logistics Base | GA0950035 | DOUGHERTY | 3350 | 126.843 | 0 | 0 | 121.9644 | 30.449 | 16.89 | 0 | 1.5246 | 48.8636 | 73.1009 | 0.6886 | 72.4123 | 74.6254 | 32.5 | 320 | 64.6 | 155394.01 | 0.32 | 452.3 | Note 3 | 220.35 | 32752.07 | VPC | 61.19% | 21.66% | 5.8955 | N/A | 6104.3008 | 72.4123 | Note 3 | 30.8092 | Volume from own sources | Billed metered | Billed unmetered | 6 | 3 | n/a |  | n/a |  | 1 | 6 | n/a | 5 | 5 | 3 | 5 | 9 | 7 | 10 | 8 | 5 | 7 | 2 | This installation does not operate like a municipality. We have limited number of "billable customers". We are attempting to improve our operations by replacing old infrasturture and install meters. This will help us more accurately quantify usage and identify leaks. QWLA - I had very limited amount of time to work on comments for this audit but, I did sit down with MCLB personnel (phone call) and we went through the audit line by line to make sure that everything was done properly and with the information available. I will however, in the near future go back over each line item and make comments that are necessary and just for this audit. If you have any questions please feel free to contact me anytime. | USMC-LB (0950035) Worksheet 2015.xls | 5
Valdosta | GA1850002 | LOWNDES | 51691 | 3414.654 | 0 | 28.9 | 3385.754 | 2527.232 | Note 1 | 1 | 42.3219 | 2570.5539 | 815.2001 | 14.7825 | 800.4176 | 858.522 | 421 | 22009 | 63 | 2375244 | 1.42 | 262.67 | 128.2882 | 28061.02 | 210245.69 | VPC | 25.36% | 10.51% | 1.8402 | 99.6376 | N/A | 800.4176 | 6.2392 | 56.6444 | Volume from own sources | Billed metered | Unbilled metered | 4 |  | n/a |  | 5 |  | 7 | n/a | 5 | 5 | 5 | n/a | 5 | 10 | 9 | 10 | 5 | 5 | 7 | 5 | QWLA Brandon Rice 2295396976 rice.brandon79@yahoo.com QWLA number 0038 note: Operator seems to know his system very well and has had help from Will Jernigan in past about audit. The audit seems to be correctly graded.[CRUC converted: $/100 cubic feet (ccf) to $/1000 gallons (US)] | Valdosta 2015 Water Audit.xls | 5
Vidalia | GA2790002 | TOOMBS | 13050 | 564.69 | 0 | 0 | 570.3939 | 464.161 | Note 1 | 14.531 | 7.1299 | 485.8219 | 84.572 | 12.3556 | 72.2164 | 106.2329 | 141 | 7023 | 42 | 712572.14 | 2.81 | 233.72 | 27.8433 | 34719.27 | 16878.42 | VPC | 18.62% | 7.952% | 4.82 | 28.1722 | N/A | 72.2164 | 2.5937 | 67.5333 | Volume from own sources | Customer metering inaccuracies | Variable production cost (applied to Real Losses) | 6 | 2 | n/a |  | n/a |  | 7 | n/a | 6 | 5 | 5 | 3 | 5 | 5 | 6 | 10 | 3 | 9 | 6 | 5 | ROBERT AKINS QWLA#0048 rlakins@esginc.net Interview with Bill Bedingfield City Clerk/Finance Director City of Vidalia | Vidalia Water Audit 2015.xls | 5
Vienna | GA0930004 | DOOLY | 3973 | 701.23 | 0 | 0 | 694.5622 | 566.723 | 0.432 | 4 | 8.682 | 579.8371 | 114.7251 | 6.0212 | 108.704 | 127.4072 | 76 | 1475 | 52.6 | 495942 | 2.1 | 145.48 | 12.1416 | 12644.45 | 15814.25 | VPC | 18.34% | 6.11% | 11.184 | N/A | 3918.6726 | 108.704 | 8.953 | 65.2495 | Billed metered | Unbilled metered | Customer metering inaccuracies | 8 | 2 | n/a | 10 | n/a | 10 | 7 | 7 | 4 | 5 | 5 | 4 | 5 | 4 | 8 | 10 | 4 | 9 | 5 | 4 | QWLA: Tal Woodall GRWA - - All inputs, grading, and comments were discussed and agreed upon with Public Works Director, Nathan Jordan. The performance indicators well represent the data and water loss efforts by the utility personnel. Real loss (gal/mi/d), Apparent loss (gal/conn/d), and ILI all fall in the middle of their respective range. 2/15/2016 | Vienna 2015 Water Audit.xls | 5
Villa Rica | GA0450006 | CARROLL | 13996 | 114.4 | 464.87 | 0 | 579.27 | 569.52 | 0 | 0.521 | 3.306 | 573.347 | 5.923 | 3.122 | 2.801 | 9.75 | 80.7 | 6223 | 83 | 1583112.59 | 5.16 | 229.94 | 41.5053 | 16109.39 | 14453.29 | CRUC | 1.683% | 3.178% | 1.3745 | 1.2332 | N/A | 2.801 | 0.067486 | 61.0784 | Water imported | Billed metered | Variable production cost (applied to Real Losses) | 7 | 3 | 7 | 3 | n/a |  | 3 | n/a | 7 | 3 | 5 | 5 | 5 | 5 | 7 | 10 | 6 | 8 | 8 | 4 | QWLA is Chris Todd (#0141) | Villa Rica, City of Worksheet 2015.xls | 5
Walker County Water & Sewerage Authority | GA2950003 | WALKER | 36000 | 1389 | 0 | 369 | 1043.7031 | 642 | Note 1 | 1.687 | 13.0463 | 656.7333 | 386.9698 | 17.3507 | 369.6191 | 401.7031 | 429.4 | 11106 | 115 | 3659267 | 3.75 | 394.24 | 167.4363 | 65065.23 | 145718.63 | VPC | 38.49% | 5.919% | 4.2802 | N/A | 2358.3024 | 369.6191 | 2.2075 | 73.6892 | Billed metered | Water exported | Customer metering inaccuracies | 4 | 5 | n/a |  | 4 | 3 | 10 | n/a | 8 | 5 | 5 | 9 | 5 | 5 | 7 | 10 | 3 | 10 | 6 | 10 | Water Audit certified by Carlos R. Haney QWLA # 0158. After conducting this water audit, the Walker County Water Authority has talked with me about implementing a strong leak detection program. Walker County Water & Sewerage Authority has experienced more water main breaks and SCADA errors in 2015 than the previous year. | Walker Co 2015 Water Audit.xls | 5
Walthourville | GA1790020 | LIBERTY | 3858 | 111.069 | 0 | 0 | 111.069 | 97.524 | 0 | 0 | 1.3884 | 98.9124 | 12.1566 | 1.0116 | 11.1451 | 13.545 | 57.2 | 2315 | 44 | 670133 | 2.2 | 414.16 | 10.5466 | 2225.42 | 4615.85 | VPC | 12.2% | 1.107% | 1.1971 | 13.1898 | N/A | 11.1451 | 1.0567 | 46.7556 | Volume from own sources | Billed metered | Customer metering inaccuracies | 3 | 2 | n/a |  | n/a |  | 1 | n/a | 10 | 5 | 5 | 2 | 5 | 2 | 3 | 10 | 3 | 10 | 4 | 10 | QWLA 0071: Spencer Senerman. Public Works Director is Jimmie Martin. Deputy Clerk is Nelean Lewis. The Finance Clerk is Margaret Bess. General Comments: City personnel should meet once per month to compare well production volumes to billed metered volumes to ensure the correct numbers are recorded for next year's audit. QWLA has concerns regarding the accuracy of the reported billed metered volume due to several errors found in the billing reports. These errors likely caused the billed metered volume to be over-stated, resulting in unreliable performance indicators. Walthourville should also consider testing its production meters every other year and incorporating the results of the meter testing into the water audit. | Walthourville, City of Worksheet 2015.xls | 5
Walton County Water Department | GA2970008 | WALTON | 37032 | 0 | 1849 | 355 | 1509.0909 | 997 | 0 | 0 | 18.8636 | 1015.8636 | 493.2273 | 10.1688 | 483.0585 | 512.0909 | 541 | 15984 | 94 | 7862521.39 | 9.66 | 1350 | 182.6805 | 98230.13 | 652129 | VPC | 33.93% | 9.867% | 1.743 | N/A | 2446.2995 | 483.0585 | 2.6443 | 75.8006 | Billed metered | Customer retail unit cost (applied to Apparent Losses) | Water imported | n/a |  | 9 | 3 | 8 | 3 | 7 | n/a | n/a | 5 | 5 | 4 | 5 | 5 | 5 | 10 | 5 | 8 | 6 | 10 | QWLA - William M Jordan, 770 466 4887, P.O. Box 880, Loganville, GA 30052 All number metrics in the 10 step level 1 validation review in line with expected output ranges. Real losses per service connection per day calculated at 48.04 (software defaults to N/A). Real Losses per service connection per day per psi pressure calculated at 8800 (software defaults to N/A). Water volume down slightly due to an extremely wet fall and winter. Also volume down throughout Atlanta area over 10% over last ten years due to weather, economy and heavy emphasis on conservation. Non revenue water by volume at 25% is in line with average for state. Apparent loss just under median and on the low side of expected range. | Walton County Water Audit 2015.xls | 5
Warner Robins | GA1530007 | HOUSTON | 64163 | 2649.917 | 802.041 | 0 | 3451.958 | 2637.047 | 0 | 0 | 43.1495 | 2680.1965 | 771.7615 | 69.0398 | 702.7217 | 814.911 | 303.8 | 26380 | 62 | 6300245 | 1.95 | 409.08 | 126.7406 | 134627.61 | 287469.4 | VPC | 23.61% | 6.98% | 7.1702 | 72.982 | N/A | 702.7217 | 5.5446 | 59.8673 | Volume from own sources | Water imported | Customer metering inaccuracies | 6 | 3 | 2 | 1 | n/a |  | 5 | n/a | n/a | 5 | 5 | 3 | 5 | 7 | 6 | 10 | 9 | 10 | 8 | 4 | QWLA: Multiple significant differences exist between values found on the 2014 and current 2015 year audits. These mainly relate to Cost Data and Validity Score. The previous auditor no longer is employed with the City, so some reasoning for previous values cannot be determined. Costs data were gathered from the City Finance Department and the budget investigated in detail. The variable production costs now includes a wighted portion of purchased import flow, which the City pays a premium for. The rise in validity score is due primarily to the "Volume from own source" score, which rose from a 3 to a 6. The " Average Operating Pressure" and "Customer retail unit cost" scores also went up. All other scores stayed the same or fell. The ILI also fell due to the changed average system pressure value provided by looking at the water model in conjunction with SCADA system monitoring points. All performance indicators fall within acceptable range except for customer retail unit, which is a little low. However, this value is per the City's published rates, not including any base charges. | Warner Robins Worksheet 2015.xls | 5
Washington | GA3170002 | WILKES | 4134 | 327.2 | 0 | 0 | 326.384 | 217.134 | 0 | 3 | 4.0798 | 224.2138 | 102.1702 | 3.5824 | 98.5879 | 109.25 | 51.6 | 2968 | 80.5 | 1462259 | 4.51 | 611.61 | 21.2834 | 16156.49 | 60297.33 | VPC | 33.47% | 5.525% | 3.3068 | 91.0053 | N/A | 98.5879 | 4.6322 | 50.2374 | Volume from own sources | Customer metering inaccuracies | Billed metered | 6 | 3 | n/a | n/a | n/a | n/a | 5 | n/a | 6 | 5 | 5 | 3 | 5 | 3 | 5 | 10 | 3 | 6 | 6 | 4 | QWLA: Alex Wiseman - Registration # 0066. All mandatory data for audit validation submitted by City. Validation date 02/29/2016. Review of performance indicators: normalized apparent losses within expected range, normalized real losses within expected range, CRUC & VPC within expected ranges, and ILI within expected range. | Washington 2015 Water Audit.xls | 5
Waycross Water System | GA2990002 | WARE | 19900 | 763.209 | 0 | 0 | 803.3779 | 731.131 | 0 | 31.265 | 10.0422 | 772.4382 | 30.9397 | 19.3954 | 11.5443 | 72.2469 | 140 | 8579 | 48 | 700000 | 1.28 | 158.63 | 35.8153 | 33187.64 | 1831.27 | VPC | 8.993% | 5.939% | 6.194 | 3.6867 | N/A | 11.5443 | 0.32233 | 58.4804 | Volume from own sources | Billed metered | Customer metering inaccuracies | 6 | 3 | n/a |  | n/a |  | 4 | n/a | 8 | 5 | 5 | 3 | 5 | 6 | 4 | 10 | 3 | 8 | 4 | 8 | GA 2990002, City of Waycross Water System. QWLA #0022 Will Corbitt[CRUC converted: $/100 cubic feet (ccf) to $/1000 gallons (US)] | Waycross, City of Worksheet 2015.xls | 5
Waynesboro | GA0330004 | BURKE | 5813 | 254.614 | 0 | 0 | 270.866 | 212.43 | 0 | 21.36 | 3.3858 | 237.1758 | 33.6901 | 5.9795 | 27.7107 | 58.436 | 81.4 | 2321 | 45 | 894637 | 5.21 | 1090.29 | 12.9515 | 31153.01 | 30212.66 | VPC | 21.57% | 9.875% | 7.0582 | N/A | 932.6737 | 27.7107 | 2.1396 | 55.1646 | Volume from own sources | Variable production cost (applied to Real Losses) | Customer metering inaccuracies | 3 | 3 | n/a |  | n/a |  | 8 | n/a | 7 | 5 | 5 | 6 | 5 | 9 | 7 | 10 | 1 | 10 | 6 | 5 | QWLA: Tal Woodall -- All Information and supporting documents to complete this Water Audit were reviewed and verified with Water Operator, Kyle Alexander. The crucial performance indicators are all on the low end of the expected ranges. These results are supported by the lack of source meter testing. The main production metere is approxamtely 8 years old and the inaccuracy is unknown. It is recommened to have the meter tested and/or calibrate or replaced. Due to the year-end expense report not being available for review the Total Operating Cost and Variable Productions Costs had to be determined using the annual budget figures. It is recommended to review the policies and procedures with the accounting department to have the yearly figures available for future Water Loss Audits. The performance indicators are expected to improve following source meter repairs and AMR installation. | Waynesboro 2015 water audit.xls | 5
West Point | GA2850002 | TROUP | 3929 | 488.56 | 11.224 | 0 | 504.8323 | 489.988 | 0 | 0 | 6.3104 | 496.2984 | 8.5339 | 7.4364 | 1.0975 | 14.8443 | 75 | 2279 | 80 | 1815764 | 3.25 | 358.75 | 21.8299 | 32308.42 | 4768.2 | CRUC | 2.94% | 3.552% | 8.9398 | N/A | 40.0911 | 1.0975 | 0.050275 | 62.5741 | Volume from own sources | Customer metering inaccuracies | Variable production cost (applied to Real Losses) | 7 | 3 | 4 | 6 | 5 |  | 6 | 10 | 8 | 5 | 5 | 4 | 5 | 8 | 6 | 10 | 4 | 10 | 6 | 4 | QWLA (Jason Clifton) conducted survey on 2/29/16. Survey was conducted with information that was obtained for the City of West Point. The information showed that there was a issue somewhere in the system because more water is being sold that is being put out into the system. The utility understand that this is a descrepincy and is working towards determining why the numbers are so far off some months.[CRUC converted: $/100 cubic feet (ccf) to $/1000 gallons (US)] | West Point 2015 Water Audit.xls | 5 |  | Negative ILI value is due to meter inaccuracies.
White County Water & Sewerage Authority | GA3110072 | WHITE | 4420 | 229.716 | 0 | 56.075 | 173.641 | 143.887 | 0 | 6.215 | 2.1705 | 152.2725 | 21.3685 | 8.6939 | 12.6746 | 29.754 | 160.2 | 2075 | 100 | 1312452.59 | 5.7 | 1275 | 42.9945 | 49555.37 | 16160.07 | VPC | 17.14% | 5.822% | 11.479 | N/A | 216.7592 | 12.6746 | 0.29479 | 66.1765 | Volume from own sources | Customer metering inaccuracies | Billed metered | 5 | 5 |  |  | 4 | 1 | 6 |  | 6 | 5 | 5 | 2 | 5 | 8 | 5 | 10 | 6 | 10 | 5 | 5 |  | White Co. 2015 Water Audit.xls | 5
Winder | GA0130002 | BARROW | 32971 | 1381.633 | 125.981 | 0 | 1507.614 | 1225.155 | 0 | 19.112 | 36.586 | 1280.853 | 226.761 | 32.2251 | 194.5359 | 282.459 | 393.6 | 15478 | 70 | 8454545.02 | 6.3 | 339.18 | 113.725 | 203018.3 | 65982.68 | VPC | 18.74% | 3.405% | 5.7041 | 34.4344 | N/A | 194.5359 | 1.7106 | 67.6307 | Volume from own sources | Customer metering inaccuracies | Variable production cost (applied to Real Losses) | 7 |  | 3 |  | n/a |  | 7 | n/a | 9 | 6 | 5 | 3 | 5 | 8 | 8 | 10 | 5 | 9 | 8 | 5 | QWLA: Tabatha Knight # 0133 | Winder 2015 Water Audit.xls | 5
Woodstock Water | GA0570003 | CHEROKEE | 10070 | 0 | 701.768 | 12.727 | 689.041 | 499.264 | 3.038 | 24.387 | 8.613 | 535.302 | 153.739 | 4.2832 | 149.4558 | 186.739 | 72.53 | 6767 | 128.01 | 3139303.02 | 6.76 | 3000.03 | 65.7606 | 28954.24 | 448371.93 | VPC | 27.1% | 18.36% | 1.7341 | 60.5095 | N/A | 149.4558 | 2.2727 | 78.7456 | Water imported | Customer metering inaccuracies | Unauthorized consumption | n/a |  | 8 | 7 | 8 | 4 | 7 | 10 | 10 | 5 | 5 | 5 | 5 | 2 | 7 | 10 | 3 | 9 | 8 | 10 | Level 1 Validation performed by Janis Steinbrenner (JS), QWLA #0129 | Woodstock 2015 Water Audit.xls | 5
Explanatory Footnote for Empty Fields
|  |  |  | Note 1 | “Note 1” represents N/A. The utility does not have uses that fit into this category.
|  |  |  | Note 2 | “Note 2” indicates the utility does not know what the value for this parameter is.
|  |  |  | Note 3 | “Note 3” indicates that the intended value cannot be calculated. The software does not display a value of UARL or ILI for very small water systems with low connection density or low pressure water distribution system. In summary, the UARL or ILI calculation has not yet been proven as fully valid for very small or low pressure water distribution systems.
|  |  |  | Note 4 | “Note 4” indicates that the intended value cannot be calculated. The software does not display a value for “Annual Cost of Real Losses” because the utility does not know what the value for the “variable production cost” is.
|  |  |  | Note A | Moody Air force Base only consumes its water and does no billing. They also randomly meter certain buildings. Most of the older buildings have no meter in place
|  |  |  | Note B | The variable production cost is not applicable to this utility. Water supply is entirely purchased as bulk water imported at a defined rate. No restriction applies for volume and there are no provisions on any rate adjustment for variable production cost. The City of Griffin does the entire meter reading for Spalding County. This cost is built in through a complex rate structure based on the contract between the County and City. In summary, Spalding County does not know the value for this field.
Yellow represent negative values (anomalies). Both the utilities and EPD are aware of these negative values (i.e. negative real losses and negative ILI values). These negative values are not creditable. They are mostly due to extreme meter inaccuracies. For example, (a) over-estimation of authorized consumption, and/or (b) under-estimation of water supply, and/or (c) over-estimation of apparent losses. To resolve this issue, the utilities with negative values must (a) replace their old meters with new ones, and/or (b) perform high frequency (short intervals) recalibration and accuracy testing on a regular basis.