REVISED TOTAL COLIFORM RULE

Level 2 Assessment Form

##### General Information

| WSID: |  | System Name: |  | Date of Trigger Notification: |  |
| --- | --- | --- | --- | --- | --- |
| County: |  | System Type: |  | Assessment Date: |  |

Facility Representative:

| Presampling Conditions |  |
| --- | --- |
| Yes | No |
| Yes | No |
| Yes | No |
| Yes | No |
| Yes | No |
| Yes | No |
| Yes | No |
| Yes | No |
| Yes | No |
| Yes | No |
| Yes | No |

Have any of the following occurred at relevant facilities prior to collection of Total Coliform samples?

- Were there any operation and maintenance activities that could have introduced total coliforms?..........................................

- Has the system lost pressure to less than 20 psi?....................................................................................................................

- Has there been any vandalism and/or unauthorized access to facilities?.................................................................................

- Are there any visible indicators of unsanitary conditions observed?.........................................................................................

Standing water	 Lab area dirty		 Surface water accessing finished water basins/units	 Other

- Have there been any analytical results or any additional (special or routine) samples collected, including source samples which were positive?..................................................................................................................................................................

- Have there been any sites with low or inadequate disinfectant residual? Are there sites where it is difficult to maintain a residual without flushing?...........................................................................................................................................................

- Were any other water quality parameters measured?...............................................................................................................

If yes, were any results out of the ordinary?	 Yes	 No

- Has there been any community illness suspected of being waterborne?..................................................................................

(e.g. Does the community public health official indicate that an outbreak has occurred?)

- Did the water system receive any Revised Total Coliform Rule violations in the past 12 months?...........................................

If yes, when?	Date:

- What was the most recent date on which satisfactory total coliform samples were taken?	Date:

- Has there been a fire fighting event, flushing operation, sheared hydrant, etc.?.......................................................................

| Other comments on records and maintenance………………………………………………………………………………………… Yes | No |
| --- | --- |
| Yes | No |
| Yes | No |
| Yes | No |
| Yes | No |
| Yes | No |

Environmental Events

- Has there been heavy rainfall?..................................................................................................................................................

- Has there been any flooding?....................................................................................................................................................

- Have there been any changes in available source water (e.g. significant drop in water table, well levels, reservoir capacity, etc.)?..........................................................................................................................................................................................

- Have there been any interruptions to electrical power?.............................................................................................................

- Have there been any extremes in heat or cold?........................................................................................................................

- Was the water colored, cloudy or have an odor?.......................................................................................................................

Identified Corrective Actions and Comments:

| Source Yes | No |
| --- | --- |
| Yes | No |

Treatment Change/Problems

- Have any inactive sources recently been introduced into the system (e.g., auxiliary systems)?...............................................

- Have there been any new sources introduced into the system?...............................................................................................

Source – Wells     N/A

- Total number of wells?

- How are the wells used? (Please indicate number of wells used for each category)

| Primary: Back-up: Emergency: Other (Not a PWS, Not Drinking Water): Yes | No |
| --- | --- |
| Yes | No |
| Yes | No |
| Yes | No |
| Yes | No |
| Yes | No |
| Yes | No |
| Yes | No |

- Are any of the wells prone to flooding?......................................................................................................................................

- Are the sanitary seals intact?.....................................................................................................................................................

- Are the well caps vented?..........................................................................................................................................................

- Does the vent terminate inside a building?................................................................................................................................

- Does the vent terminate twelve (12) inches above the well pad?..............................................................................................

- Are the vents screened and are the screens intact?..................................................................................................................

- Does the pump to waste terminate in approved air gaps?.........................................................................................................

- Are there any unprotected cross connections at the wellhead?................................................................................................

- How far does the casing extend above grade? (Please indicate in inches)

Well 1 Height:      		Well 2 Height:      		Well 3 Height:      		Well 4 Height:

| Well 5 Height: Well 6 Height: Well 7 Height: Well 8 Height: Yes | No |
| --- | --- |
| Yes | No |
| Yes | No |
| Yes | No |
| Yes | No |
| Yes | No |

- Is there evidence of standing water near the wellhead?............................................................................................................

- Are the wellheads secured to prevent unauthorized access?....................................................................................................

- Has the well pump been replaced? …………………………………………………………………………………………….………..

If so, when?

- Have there been any spills or contaminants released within the protection area?....................................................................

- Can the positive samples be attributed to well construction?....................................................................................................

- Other comments on the well system……………………………………………………………………………….…………………….

Source – Purchased Water Connection (Consecutive System)     N/A

- Please list the Water System name and WSID# for each purchased water source in use within the last sixty (60) days:

| Do the physical connections show signs of contamination (e.g. flooded vault, leaking valves, recent maintenance, etc.)?.... Yes | No |
| --- | --- |

Source – Springs     N/A

- What is the sanitary condition at the source?

No problems seen		 Areas need maintenance

- What is the condition of the intake?

| No problems seen Areas need maintenance Yes | No |
| --- | --- |
| Yes | No |

- Is the source secured to prevent unauthorized access?............................................................................................................

- Other comments on the spring system……………………………………………………………………………………………….….

| Source – Surface Water Supply N/A Yes | No |
| --- | --- |
| Yes | No |
| Yes | No |
| Yes | No |

- Have there been any spills (i.e. sewer, petroleum) or contaminants released within the watershed?.......................................

- Have there been any algal blooms?..........................................................................................................................................

- Has source water turnover occurred?........................................................................................................................................

- Other source water comments……………………………………………………………………………………………………………

Identified Corrective Actions and Comments:

Treatment	  N/A

| Number of treatment plants: Yes | No |
| --- | --- |
| Yes | No |
| Yes | No |
| Yes | No |
| Yes | No |
| Yes | No |

- Treatment devices operational and maintained?.......................................................................................................................

- Is there any recent installation or repair of treatment equipment?.............................................................................................

- Were there any recent changes in the treatment process? (e.g. addition of a process, change in chemical or dosage)……...

If yes, when, what was the change?

- Have there been any interruptions in the treatment process (lapse in chemical feed, disinfection, turbidity excursions, etc.).. If yes, for how long?

Chemical feed problems				 Chemical added/changed			 Disinfectant added/changed

Abnormal flow rates/short circuiting		 Clearwell operational issues		 Abnormal influent turbidity

Excessive filter run-time				 Filters operated above capacity	 Sludge blanket carryover

Coagulation/sedimentation problems	 Other

- What is the free chlorine residual measured at each entry point?

Entry point 1:      	Entry point 2:      	Entry point 3:      	Entry point 4:

Entry point 5:      	Entry point 6:      	Entry point 7:      	Entry point 8:

- Were there any failures to meet the contact time (CT) requirements?  N/A……………………………………………….........

- Were the flow rates above the rated capacity?  N/A............................................................................................................

Treatment (Continued)

| Did a review of the filter turbidity profiles reveal any anomalies? N/A………………………………………………………….. Yes | No |
| --- | --- |
| Yes | No |
| Yes | No |

- Were there any anomalies on the settled water turbidities?  N/A………………………………………………………….……..

- Other comments on the treatment system………………………………………………………………………………………………

Identified Corrective Actions and Comments:

Distribution

| Distribution System Yes | No |
| --- | --- |
| Yes | No |
| Yes | No |
| Yes | No |
| Yes | No |
| Yes | No |
| Yes | No |
| Yes | No |
| Yes | No |
| Yes | No |
| Yes | No |
| Yes | No |
| Yes | No |
| Yes | No |
| Yes | No |
| Yes | No |

- Was the sample collected in a hydraulically isolated area of the distribution system?...............................................................

- System pressure: Is there evidence that the system experienced low or negative pressure?...................................................

If yes, when?	Date:

- Were any cross connections identified?.....................................................................................................................................

- Pump station (if applicable): Are there any sanitary defects in the pump station(s)?  N/A…………………………………….

- Last pump maintenance/service date:

- Air relief valves: Is the valve vault subject to flooding or does the vent terminate below grade?...............................................

- Have there been any operating issues with control valves (i.e. Pressure Reducing Valves, Altitude)?.....................................

- Fire hydrant/blow off: Are any located in an area with a high water table or pits?......................................................................

- Is the distribution system secured to prevent unauthorized access?.........................................................................................

- Are the backflow prevention devices at high risk sites present, operational and maintained?...................................................

- Have there been any water main repairs or additions? If yes, explain the type of repair or addition below………..……………

- Have there been any water main breaks?.................................................................................................................................

If yes, when?	Date:

- Was there any scheduled flushing of the distribution system?...................................................................................................

If yes, when?	Date:

- Is there any evidence of intentional contamination in the distribution system?..........................................................................

- Does the booster chlorinator function properly?   N/A...........................................................................................................

- Is there evidence of loss of disinfection or other potential sources of contamination?...............................................................

- Other comments on the distribution system……………………………………………………………………………………………..

Identified Corrective Actions and Comments:

| Storage Facilities Yes | No |
| --- | --- |
| Yes | No |
| Yes | No |
| Yes | No |
| Yes | No |
| Yes | No |
| Yes | No |
| Yes | No |
| Yes | No |
| Yes | No |
| Yes | No |
| Yes | No |
| Yes | No |

- How many storage tanks are in the system?

- Are the overflow and vents properly screened?.........................................................................................................................

- Is the facility secured to prevent unauthorized access?.............................................................................................................

- Is the access opening sealed tightly?........................................................................................................................................

- Was there any observed physical deterioration of the tank?.....................................................................................................

- Could the physical condition of the tank be a source of contamination?....................................................................................

- Is the vent turned down and maintaining an approved air gap at the termination point?...........................................................

- Are there any unsealed openings in the storage facility such as access doors, vents, or joints?..............................................

- Does the drain/overflow line fail to provide the minimum of a 12-inch air gap?.........................................................................

- If present, did the pressure tank deviate from normal operating pressure?...............................................................................

If yes, how much?

- Were there any observed leaks?...............................................................................................................................................

| Is there any evidence of vandalism or intentional contamination at the storage tank?.............................................................. Yes | No |
| --- | --- |
| Yes | No |

- Does it appear as though proper operation and maintenance activities are being performed?.................................................

- Has there been any facility maintenance? (i.e. painting/coating)…………………………....………………………….……………

If yes, when?

- When was last tank inspection?	Date:

- Was the required microbiological sampling conducted before returning the tank to service?....................................................

- Does the tank on the distribution system have a single inlet/outlet or are there separate inlet and outlet lines?

Single	 Separate

- What is the measured free chlorine residual of the water exiting the storage tank today?

Tank 1:      		Tank 2:      		Tank 3:      		Tank 4:

Tank 5:      		Tank 6:      		Tank 7:      		Tank 8:

- Other comments on the storage system…………………………………………………………………………………………………

Identified Corrective Actions and Comments:

##### Sampling

| Sample Site Yes | No |
| --- | --- |
| Yes | No |
| Yes | No |
| Yes | No |
| Yes | No |
| Yes | No |
| Yes | No |
| Yes | No |
| Yes | No |
| Yes | No |

- Have conditions changed at the sample site since last sample collection?................................................................................

- What is the location of the tap?

Outside residence		 Outside business		 Yard spigot

Inside residence		 Inside business			 Other (explain in comments)

- What is the regular use of the connection?

Kitchen			 Bathroom				 Irrigation			 Landscape		 Sampling Only

- Was there a potential for hot water to enter the sample through the tap?..................................................................................

- Have there been any plumbing changes or construction?..........................................................................................................

If yes, when and what was the repair or change?

- Have there been any plumbing breaks or failure?......................................................................................................................

If yes, when?	Date:

- Were any cross connections identified after the service connection or in premise plumbing?...................................................

- Were all of the backflow prevention devices present, operational and maintained?..................................................................

- Have there been any operating issues with control valves (i.e. Pressure Reducing Valves, Altitude)?.....................................

- Were there any low pressure events or changes in water pressure after the service connection or in the premise plumbing?

If yes, when?	Date:

- Are there any treatment devices after the service connection or in premise?............................................................................

If yes,  Point of Entry		 Point of Use

- Other comments on sample site?...............................................................................................................................................

Identified Corrective Actions and Comments:

| Sample Protocol Yes | No |
| --- | --- |
| Yes | No |
| Yes | No |
| Yes | No |
| Yes | No |
| Yes | No |
| Yes | No |
| Yes | No |

- Were all Total Coliform samples collected and handled using proper Standard Operating Procedures?..................................

- Did sample collection and handling factors contribute to contamination?..................................................................................

- Were there any visible indicators of unsanitary conditions?.......................................................................................................

- Were sterile sample bottles used?.............................................................................................................................................

- Were the samples transported in a sanitized cooler or clean box?............................................................................................

- Were there any changes in sampler or collection protocol?......................................................................................................

- Was the sample tap disinfected before use?.............................................................................................................................

- Were samples shipped properly to avoid contamination?..........................................................................................................

- What was the free chlorine residual at the positive sample site/sites?

| Positive Sample Site No. | Free Chlorine Residual Result |
| --- | --- |

Sample Tap

| What is the condition of the tap? Yes | No |
| --- | --- |
| Yes | No |
| Yes | No |
| Yes | No |
| Yes | No |

No problems seen			 Areas need maintenance

- Was the tap flushed to ensure that a representative sample was collected?.............................................................................

- Was the tap flushed during Level 2 Assessment visit?  How long did it actually take to flush the tap to ensure that a free chlorine residual was present?………........................................................................................................................................

Time:

- Was the aerator removed before collection?  N/A................................................................................................................

- Was the sample collected from a swivel faucet?........................................................................................................................

- Was the sample tap leaking or broken?.....................................................................................................................................

Identified Corrective Actions and Comments:

Certification: I certify under penalty of law that I am the person authorized to fill out this form, and the information contained herein is true, accurate and complete to the best of my knowledge and belief.

| Completed by: |  | Title: |  |
| --- | --- | --- | --- |
| Signature: |  | Date: |  |

| Reviewed by: |  | Title: |  |
| --- | --- | --- | --- |