## Filtration
Georgia Environmental Protection Division
SURFACE WATER TREATMENT OPERATION REPORT for MEMBRANE FILTRATION
System Name: |  | City of Carrollton |  | WSID # : | 0450002 | Month : | May
Treatment Facility Name: |  |  | City of Carrollton Waterworks | Plant # : | 201 | Year: | 2014
I - INTEGRITY TESTING
(a) | Number of direct integrity tests performed | [5 empty] | 127
(b) | Number of failed direct integrity tests
II - CONTINUOUS MONITORING OF PLANT FILTRATE
(a) | Was continuous monitoring and recording of plant filtrate performed? |  |  |  |  | Yes |  | No
III - CONTINUOUS INDIRECT INTEGRITY MONITORING
(a) | Was each membrane unit continuously monitored for turbidity? |  |  |  |  | Yes |  | No
(b) | Was each membrane filter monitoring result recorded every 15 minutes ? |  |  |  |  | Yes |  | No
( c) | Were at least 95 % of individual samples from each membrane unit less than or equal to 0.10 NTU?
[6 empty] | Yes |  | No
(d) | Were any two consecutive 15 minute filtrate turbidity readings above 0.15 NTU?
[6 empty] | Yes |  | No
If YES, was direct integrity testing initiated to isolate the integrity breach?
[6 empty] | Yes |  | No
(e) | Attach report of 95% percentile of monthly turbidity values for each membrane unit, along with a summary of all excursions above 0.15.
|  |  | Submitted by: |  |  | Date:
Certification No:
Ga. EPD - MOR/p.11 |  |  | Certification Class:

## 95th Percentile
Georgia Environmental Protection Division
SURFACE WATER TREATMENT OPERATION REPORT for MEMBRANE FILTRATION
System Name: |  | City of Carrollton |  |  | WSID # : | 0450002 | Month : | May
Treatment Facility Name: |  |  | City of Carrollton Waterworks |  | Plant # : | 201 | Year: | 2014
95th Percentile Values for Each Turbidity Unit (copy this sheet if needed)
Unit | 95th Percentile of Turbidity (NTU)
ZW1 | 0.037
ZW2 | 0.067 |  |  | Summary of all excursions above 0.15
ZW3 | 0.03 |  |  | MIT's, Air, Backwash's, Standby mode and Off.
ZW4 | 0.066