## 2023 Water Loss Audits
Name of City / Utility: 2023 Validated Water Audit | WSID Number | Service County | Water System Service Population | Volume From Own Sources | Water Imported | Water Exported | Water Supplied | Billed Metered | Billed Unmetered | Unbilled Metered | Unbilled Unmetered | Authorized Consumption | Water Losses | Annual Volume of Apparent Losses | Annual Volume of Real Losses | Non Revenue Water | Length of Mains | Number of Active and Inactive Service Connections | Average Operating Pressure | Total Annual Cost of Operating Water System | Customer Retail Unit Cost | Variable Production Cost | Unavoidable Annual Real Losses (UARL) vol/Yr | Annual Volume of NRW | Annual Cost of Apparent Losses | Annual Cost of Real Losses | Annual Cost of NRW | Value Applied to Real Losses (VPC / CRUC) | Unit Apparent Losses Vol/conn/day | Unit Real Losses Vol/conn/day | Unit Real Losses per length of main per day | Total Loss Cost Rate $/conn/yr | Apparent Loss Cost Rate $/conn/yr | Real Loss Cost Rate $/conn/yr | Infrastructure Leakage Index (ILI) | Water Audit Data Validity Score
Adairsville | GA0150000 | Bartow | 7306 | 641.35 | 16.4803 | 218.7991 | 437.506 | 287.636 | 0.036 | 6.953 | 2.3 | 296.925 | 140.5811 | 10.5494 | 130.0317 | 149.8341 | 89.3 | 3599 | 70 | Note 2 | 9.21 | 743.08 | 26.1367 | 149.8341 | 95338.86 | 96623.96 | 198838.54 | VPC | 8.0307 | 98.9862 | 3989.3755 | 53.3378 | 26.4904 | 26.8474 | 4.9751 | 76
Adel | GA0750000 | Cook | 6560 | 358.907 | Note 1 | Note 1 | 358.907 | 279.453 | Note 1 | 0.758 | 0.69863 | 280.9096 | 77.9974 | 1.3973 | 76.6001 | 79.454 | 74.5 | 3058 | 54 | 854605 | 2.34 | 3.16 | 16.985 | 79.454 | 3269.6 | 242.06 | 3516.26 | VPC | 1.2518 | 68.6276 | 2816.957 | 1.1484 | 1.0692 | 0.079155 | 4.5099 | 44
Alamo | GA3090000 | Wheeler | 3260 | 151.394 | Note 1 | Note 1 | 154.8788 | 153.113 | Note 1 | Note 1 | 0.38278 | 153.4958 | 1.383 | 1.1493 | 0.23368 | 1.7658 | 25 | 358 | 45 | 161585.53 | 3.46 | 223.71 | 3.1035 | 1.7658 | 3976.6 | 52.28 | 4114.51 | VPC | 8.7955 | 1.7883 | 25.6091 | 11.2539 | 11.1078 | 0.14603 | 0.075297 | 73
Albany | GA0950000 | Dougherty | 92208 | 4720.851 | Note 1 | Note 1 | 4937.6122 | 3901.182 | Note 1 | 69.24 | 65.075 | 4035.497 | 902.1152 | 100.5349 | 801.5802 | 1036.4302 | 677.9 | 38580 | 55 | 12361200 | 5.87 | 228.1 | 189.7979 | 1036.4302 | 582167.69 | 4705276.03 | 6075872.77 | CRUC | 7.1394 | 56.9235 | 3239.5785 | 137.0514 | 15.0899 | 121.9615 | 4.2233 | 61
Alma | GA0050000 | Bacon | 5239 | 217.317 | Note 1 | Note 1 | 221.526 | 163.585 | Note 1 | 27.65 | 22.22 | 213.455 | 8.071 | 3.7301 | 4.3409 | 57.941 | 48 | 2015 | 60 | 498024 | 5.78 | 200.26 | 12.3063 | 57.941 | 19210.73 | 869.3 | 30067 | VPC | 5.0717 | 5.9021 | 247.766 | 9.9653 | 9.5339 | 0.43141 | 0.35274 | 86
Americus | GA2610000 | Sumter | 33292 | 937.22 | Note 1 | Note 1 | 936.9567 | 615.4538 | Note 1 | 0.032802 | 1.5386 | 617.0253 | 319.9314 | 28.7225 | 291.2089 | 321.5029 | 148.7 | 7658 | 66 | 2319786 | 4.43 | 361.88 | 47.0518 | 321.5029 | 127235.32 | 105382.68 | 233186.67 | VPC | 10.2758 | 104.1829 | 5365.384 | 30.3758 | 16.6147 | 13.7611 | 6.1891 | 58
Ashburn | GA2870000 | Turner | 7052 | 235.333 | Note 1 | Note 1 | 294.1662 | 200.975 | Note 1 | Note 1 | 11.42 | 212.395 | 81.7713 | 11.5825 | 70.1887 | 93.1913 | 57.7 | 2621 | 47.5 | Note 2 | 2.66 | 324.83 | 12.2283 | 93.1913 | 30809.47 | 22799.41 | 57318.44 | VPC | 12.1072 | 73.3682 | 3332.7197 | 20.4536 | 11.7549 | 8.6987 | 5.7399 | 61
Athens-Clarke County Public Utilities Dept | GA0590000 | Clarke | 128711 | 5034.59 | Note 1 | Note 1 | 4984.7426 | 4331.212 | Note 1 | 271.182 | 10.828 | 4613.222 | 371.5205 | 68.1449 | 303.3757 | 653.5306 | 825.179 | 43479 | 88.93 | 8218351.73 | 6.79 | 414.66 | 356.6017 | 653.5306 | 445240.38 | 125797.75 | 687976.41 | VPC | 4.294 | 19.1165 | 1007.2556 | 13.1337 | 10.2404 | 2.8933 | 0.85074 | 84
Atlanta DWM | GA1210001 | Fulton | 1200000 | 36865.39 | 5339.7 | 1482.5564 | 40764.3937 | 25811.96 | 1.384 | Note 1 | 493.411 | 26306.755 | 14457.6387 | 1571.0125 | 12886.6262 | 14951.0497 | 2822.82 | 222051 | 106.16 | 158135993.79 | 7.6723 | 334.374 | 1882.3626 | 14951.0497 | 12053276.74 | 4308952.74 | 16527213.29 | VPC | 19.3836 | 158.9987 | 12507.2889 | 73.6868 | 54.2816 | 19.4052 | 6.846 | 79
Auburn | GA0130000 | Barrow | 10441 | Note 1 | 251.28 | 1.1 | 252.0755 | 192.43 | Note 1 | Note 1 | 0.48108 | 192.9111 | 59.1645 | 1.4444 | 57.72 | 59.6455 | 80.7 | 3642 | 50.3 | 2584244.96 | 9.82 | 550 | 18.0453 | 59.6455 | 14184.31 | 31746.01 | 46194.91 | VPC | 1.0866 | 43.4204 | 1959.567 | 12.6113 | 3.8946 | 8.7166 | 3.1986 | 71
Augusta Utilities | GA2450000 | Richmond | 200000 | 13683.64 | Note 1 | Note 1 | 13140.1629 | 9308.127 | Note 1 | 1064.78 | 110 | 10482.907 | 2657.2559 | 258.2326 | 2399.0232 | 3832.0359 | 1324 | 67967 | 87 | 58822805 | 6.78 | 351.22 | 551.1998 | 3832.0359 | 1611118.43 | 842584.94 | 2866309.6 | VPC | 10.4093 | 96.7038 | 4964.2496 | 36.1014 | 23.7044 | 12.397 | 4.3524 | 70
Austell | CP0670001 | Cobb | 7800 | Note 1 | 323.84 | Note 1 | 327.045 | 266.136 | Note 1 | 3.0913 | 0.252 | 269.4793 | 57.5657 | 2.0054 | 55.5603 | 60.909 | 62.89 | 3760 | 128 | 2103995.43 | 8.46 | 6497.02 | 42.2459 | 60.909 | 16950.77 | 360976.42 | 399648.68 | VPC | 1.4613 | 40.484 | 2420.4169 | 100.5126 | 4.5082 | 96.0044 | 1.3152 | 83
Bainbridge | GA0870001 | Decatur | 15000 | 887.68 | Note 1 | Note 1 | 896.6465 | 698.459 | Note 1 | 20 | 1.7461 | 720.2051 | 176.4413 | 10.7495 | 165.6919 | 198.1875 | 190 | 5775 | 55 | Note 2 | 3.36 | 455 | 38.0251 | 198.1875 | 35531.31 | 75389.8 | 120815.6 | VPC | 5.0997 | 78.6061 | 2389.2121 | 19.2071 | 6.1526 | 13.0545 | 4.3574 | 40
Baldwin | GA1370001 | Habersham | 5014 | 722.018 | Note 1 | 489.518 | 225.2383 | 119.3 | Note 1 | 1.911 | 13.133 | 134.344 | 90.8943 | 2.3175 | 88.5767 | 105.9383 | 71.53 | 1914 | 103 | Note 2 | 12.16 | 1917.62 | 25.3419 | 105.9383 | 27903.48 | 169856.51 | 226608.66 | VPC | 3.3174 | 126.79 | 3392.646 | 103.3229 | 14.5786 | 88.7443 | 3.4953 | 77
Baldwin County Water & Sewer | GA0090000 | Baldwin | 23067 | Note 1 | 759.074 | 5.701 | 753.1967 | 551.06 | Note 1 | 9.087 | 1.3776 | 561.5246 | 191.672 | 20.0794 | 171.5926 | 202.1367 | 423 | 9752 | 60 | Note 2 | 8.77 | 1887.15 | 82.1519 | 202.1367 | 174162.27 | 323820.97 | 517731.6 | VPC | 5.6411 | 48.2072 | 1111.387 | 51.0647 | 17.8591 | 33.2056 | 2.0887 | 52
Banks County | GA0110026 | Banks | 10000 | 253.43 | 31.906 | 52.223 | 253.6974 | 216.553 | Note 1 | 27.694 | 0.54138 | 244.7884 | 8.909 | 6.0674 | 2.8416 | 37.1444 | 336 | 3298 | 99 | 1658062.24 | 7.14 | 949.12 | 83.5607 | 37.1444 | 39822.23 | 2697.06 | 69318.06 | VPC | 5.0403 | 2.3606 | 23.1706 | 12.8924 | 12.0747 | 0.81779 | 0.034007 | 62
Barnesville | GA1710000 | Lamar | 10400 | 706.35 | 4.543 | 37.825 | 673.068 | 375.706 | Note 1 | 94.222 | 0.93927 | 470.8673 | 202.2007 | 16.4124 | 185.7883 | 297.362 | 82 | 4785 | 85 | Note 2 | 6.51 | 379.42 | 36.0315 | 297.362 | 88979.62 | 70491.82 | 195577.52 | VPC | 9.3972 | 106.376 | 6207.429 | 33.3274 | 18.5955 | 14.7318 | 5.1563 | 55
Barrow County Water System / Barrow Co. BOC Transmission Mains | GA0130031,GA0130034 | Barrow | 18437 | Note 1 | 831.054 | 399.853 | 424.3584 | 401.764 | Note 1 | 3.685 | 1.0044 | 406.4534 | 17.905 | 0.95739 | 16.9476 | 22.5944 | 163.1 | 7037 | 114.8 | Note 2 | 14.65 | 810.77 | 81.2028 | 22.5944 | 14157.96 | 13740.64 | 31700.63 | VPC | 0.37274 | 6.5983 | 284.6836 | 3.9646 | 2.0119 | 1.9526 | 0.20871 | 66
Bartow County Water Department | GA0015001 | Bartow | 67673 | Note 1 | 2889.492 | 24.669 | 2908.4497 | 1969.32 | 2.838 | Note 1 | 11.9671 | 1984.1251 | 924.3246 | 39.8504 | 884.4742 | 936.2917 | 801.62 | 25064 | 126.4 | 33282313.26 | 8.743 | 3031.8886 | 373.5339 | 936.2917 | 348412.35 | 2681627.25 | 3066322.52 | VPC | 4.356 | 96.6812 | 3022.8999 | 120.8921 | 13.9009 | 106.9912 | 2.3679 | 64
Baxley | GA0010000 | Appling | 5924 | 276.395 | Note 1 | Note 1 | 277.1711 | 265.781 | Note 1 | 8.503 | 0.66445 | 274.9485 | 2.2226 | 1.4112 | 0.81141 | 11.3901 | 108.88 | 2714 | 58 | 596089 | 4.35 | 676 | 21.0883 | 11.3901 | 6129.41 | 548.51 | 12875.12 | VPC | 1.4246 | 0.8191 | 20.4174 | 2.4605 | 2.2584 | 0.20211 | 0.038477 | 71
Blackshear | GA2290000 | Pierce | 3489 | 168.883 | Note 1 | Note 1 | 167.2109 | 145.993 | Note 1 | 0.053 | 0.36498 | 146.411 | 20.7999 | 2.954 | 17.8459 | 21.2179 | 36 | 2245 | 52 | 758629.4 | 5.16 | 337.79 | 10.0881 | 21.2179 | 15238.83 | 6028.16 | 21408.18 | VPC | 3.605 | 21.7786 | 1358.1349 | 9.473 | 6.7879 | 2.6852 | 1.769 | 70
Blairsville | GA2910000 | Union | 5137 | 229.125 | Note 1 | Note 1 | 229.2626 | 149.277 | Note 1 | 4.008 | 1.824 | 155.109 | 74.1536 | 0.89982 | 73.2537 | 79.9856 | 74.6 | 1924 | 98 | Note 2 | 8.32 | 766 | 24.7595 | 79.9856 | 7456.22 | 56112.36 | 68035.9 | VPC | 1.2813 | 104.3114 | 2690.2837 | 33.0398 | 3.8754 | 29.1644 | 2.9586 | 75
Blakely | GA0990000 | Early | 8182 | 333.332 | Note 1 | Note 1 | 333.332 | 165.111 | Note 1 | 3.65 | 0.41278 | 169.1738 | 164.1582 | 0.82555 | 163.3327 | 168.221 | 56 | 3147 | 53 | 223000 | 5.41 | 317.66 | 14.9926 | 168.221 | 4466.25 | 51884.26 | 57641.09 | VPC | 0.71871 | 142.1947 | 7990.835 | 17.9061 | 1.4192 | 16.4869 | 10.8942 | 81
Blue Ridge Water & Sewer | GA1110000 | Fannin | 8000 | 315.065 | Note 1 | 14.118 | 304.8649 | 204.6774 | Note 1 | 0.78253 | 0.438 | 205.898 | 98.9669 | 2.5415 | 96.4254 | 100.1874 | 136 | 3574 | 100 | 3136204.82 | 9.08 | 766.87 | 46.4229 | 100.1874 | 23015.14 | 73945.76 | 97896.89 | VPC | 1.9482 | 73.917 | 1942.4943 | 27.1295 | 6.4396 | 20.6899 | 2.0771 | 89
Braselton | GA1570000 | Jackson | 12371 | 185.774 | 453.567 | 29.429 | 607.4759 | 573.09 | Note 1 | 1.334 | 1.4327 | 575.8567 | 31.6192 | 2.8655 | 28.7537 | 34.3859 | 141 | 6916 | 100.75 | Note 2 | 8.73 | 1519 | 66.2005 | 34.3859 | 25015.38 | 43676.9 | 72894.93 | VPC | 1.1351 | 11.3906 | 558.7043 | 9.9324 | 3.617 | 6.3153 | 0.43434 | 51
Bremen | GA1430000 | Haralson | 6700 | 103.475 | 356.679 | 88.683 | 375.9075 | 263.894 | Note 1 | 0.02 | 0.65974 | 264.5737 | 111.3338 | 1.3195 | 110.0143 | 112.0135 | 76 | 3315 | 90 | Note 2 | 5.97 | 3665.39 | 29.8413 | 112.0135 | 7877.24 | 403245.3 | 413614.03 | VPC | 1.0905 | 90.9228 | 3965.9083 | 124.0189 | 2.3762 | 121.6426 | 3.6866 | 75
Brunswick-Glynn Joint Water & Sewer | GA1270000 | Glynn | 51501 | 1941.349 | Note 1 | Note 1 | 1936.5077 | 1275.122 | Note 1 | 302.13 | 3.1878 | 1580.4398 | 356.0679 | 72.0944 | 283.9735 | 661.3857 | 344 | 20159 | 54 | 3120735 | 2.89 | 253.21 | 96.2812 | 661.3857 | 175159.05 | 71904.93 | 324373.5 | VPC | 9.7981 | 38.5937 | 2261.6556 | 12.2558 | 8.6889 | 3.5669 | 2.9494 | 60
Brunswick-Glynn Joint Water Sewer Commission-St. Simons Island | GA1270001 | Glynn | 29255 | 1047.04 | Note 1 | Note 1 | 1044.4289 | 749.157 | Note 1 | 136.66 | 1.8729 | 887.6899 | 156.739 | 40.6548 | 116.0842 | 295.2719 | 158 | 11609 | 56 | 1683126 | 2.89 | 253.21 | 53.0649 | 295.2719 | 102478.13 | 29393.68 | 166949.72 | VPC | 9.5945 | 27.3959 | 2012.9046 | 11.3594 | 8.8275 | 2.532 | 2.1876 | 60
Buford | GA1350000 | Gwinnett | 8346 | 421.679 | 13.788 | Note 1 | 435.467 | 364.939 | 1.968 | 9.141 | 0.91727 | 376.9653 | 58.5017 | 19.0925 | 39.4092 | 68.56 | 81 | 3798 | 61 | 5068112.96 | 2.46 | 671.27 | 22.4411 | 68.56 | 46213.32 | 26454.21 | 79419.34 | VPC | 13.7726 | 28.4282 | 1332.9677 | 19.1331 | 12.1678 | 6.9653 | 1.7561 | 63
Butts County Water & Sewer Authority | GA0350051 | Butts | 25968 | 908.81 | 14.773 | 88.761 | 852.7508 | 608.538 | Note 1 | 0.095 | 1.5213 | 610.1543 | 242.5965 | 9.1905 | 233.406 | 244.2128 | 320 | 6951 | 84.4 | Note 2 | 6.71 | 741.49 | 85.4512 | 244.2128 | 61662.51 | 173068.19 | 235929.21 | VPC | 3.6224 | 91.9966 | 1998.3388 | 33.7693 | 8.871 | 24.8983 | 2.7315 | 64
Byron | GA2250000 | Peach | 5690 | 302.48 | Note 1 | Note 1 | 305.5354 | 248.037 | Note 1 | Note 1 | 0.62009 | 248.6571 | 56.8783 | 3.7456 | 53.1327 | 57.4984 | 76 | 3621 | 60 | 947845 | 5 | 371.61 | 20.8994 | 57.4984 | 18728.05 | 19744.62 | 38703.1 | VPC | 2.834 | 40.2013 | 1915.3804 | 10.6249 | 5.1721 | 5.4528 | 2.5423 | 49
Cairo | GA1310000 | Grady | 10000 | 524.96 | Note 1 | Note 1 | 507.2077 | 378.87 | Note 1 | Note 1 | 0.94717 | 379.8172 | 127.3906 | 5.7213 | 121.6692 | 128.3377 | 130 | 4575 | 70 | 444317 | 1.85 | 846.38 | 35.503 | 128.3377 | 10584.44 | 102978.41 | 114364.52 | VPC | 3.4262 | 72.8613 | 2564.1567 | 24.8225 | 2.3135 | 22.5089 | 3.427 | 60
Calhoun | GA1290000 | Gordon | 60450 | 3919.963 | Note 1 | 974.089 | 2950.3899 | 2139.059 | Note 1 | Note 1 | 5.555 | 2144.614 | 805.7759 | 63.969 | 741.8069 | 811.3309 | 865.6 | 23365 | 107.4 | 12067047.9 | 4.87 | 392.17 | 320.9639 | 811.3309 | 311528.93 | 290914.41 | 604621.84 | VPC | 7.5009 | 86.9826 | 2347.9062 | 25.784 | 13.3331 | 12.4509 | 2.3112 | 71
Camilla | GA2050001 | Mitchell | 5500 | 952.778 | Note 1 | Note 1 | 976.307 | 762.896 | Note 1 | Note 1 | 1.9072 | 764.8032 | 211.5038 | 43.9669 | 167.5369 | 213.411 | 72 | 2871 | 57 | 1412681.71 | 2.39 | 276.64 | 17.0636 | 213.411 | 105080.89 | 46347.4 | 151955.91 | VPC | 41.9566 | 159.8764 | 6375.0707 | 52.7441 | 36.6008 | 16.1433 | 9.8184 | 61
Canton | GA0570001 | Cherokee | 27048 | 1330.43 | 72.241 | 153.9967 | 1292.6554 | 1130.3339 | Note 1 | 8.0931 | 2.8258 | 1141.2528 | 151.4026 | 28.8849 | 122.5177 | 162.3215 | 150 | 10300 | 80 | Note 2 | 5.93 | 697.37 | 68.8098 | 162.3215 | 170423.05 | 85440.2 | 263477.77 | VPC | 7.6832 | 32.5888 | 2237.7669 | 24.8411 | 16.5459 | 8.2952 | 1.7805 | 64
Carroll County Water Authority | GA0450001 | Carroll | 49681 | 1951.029 | 9.528 | 480.348 | 1479.2846 | 1136.804 | Note 1 | 13.865 | 63.779 | 1214.448 | 264.8366 | 17.3069 | 247.5297 | 342.4806 | 805.7 | 21006 | 97 | Note 2 | 9.11 | 544.12 | 265.8822 | 342.4806 | 156466.56 | 134685.86 | 333400.08 | VPC | 2.2573 | 32.2843 | 841.7073 | 13.8604 | 7.4487 | 6.4118 | 0.93097 | 73
Carrollton | GA0450002 | Carroll | 27493 | 1848.48 | Note 1 | 1.127 | 1843.6612 | 1499.19 | Note 1 | 41.243 | 28.933 | 1569.366 | 274.2952 | 7.496 | 266.7992 | 344.4712 | 246.3 | 11336 | 80 | 4522457.23 | 5.24 | 599.1 | 88.5602 | 344.4712 | 39278.78 | 159839.41 | 241160.63 | VPC | 1.8116 | 64.481 | 2967.7497 | 17.5651 | 3.465 | 14.1002 | 3.0126 | 69
Cartersville | GA0150002 | Bartow | 32568 | 4845.67 | Note 1 | 2599.43 | 2208.2593 | 1703.337 | Note 1 | Note 1 | 4.2583 | 1707.5953 | 500.6639 | 61.1972 | 439.4667 | 504.9223 | 238 | 12526 | 115 | 13641732 | 3.95 | 181.54 | 132.913 | 504.9223 | 323144.65 | 79780.79 | 403698.49 | VPC | 13.3852 | 96.1215 | 5058.9007 | 32.1671 | 25.7979 | 6.3692 | 3.3064 | 59
Catoosa Utility District | GA0470000 | Catoosa | 60000 | 1299.021 | 473.021 | 69.415 | 1719.7474 | 1337.936 | Note 1 | Note 1 | 3.3448 | 1341.2808 | 378.4666 | 14.3596 | 364.1069 | 381.8114 | 580 | 21942 | 113 | 7446779 | 4.41 | 457.39 | 265.1682 | 381.8114 | 63325.99 | 166538.87 | 231394.76 | VPC | 1.793 | 45.4632 | 1719.9194 | 10.476 | 2.8861 | 7.59 | 1.3731 | 63
Cave Spring | GA1150000 | Floyd | 4142 | 313.85 | Note 1 | 106.523 | 191.6506 | 78.68 | 24.602 | 5.914 | 0.25821 | 109.4542 | 82.1964 | 3.1327 | 79.0637 | 88.3686 | 87 | 2090 | 96.8 | Note 2 | 4.62 | 276.17 | 27.7063 | 88.3686 | 13678.65 | 21835.01 | 37218.24 | VPC | 4.1066 | 103.6425 | 2489.8022 | 16.9922 | 6.5448 | 10.4474 | 2.8536 | 81
Cedartown | GA2330000 | Polk | 9750 | 440.953 | Note 1 | Note 1 | 441.527 | 330.4049 | Note 1 | 52.2174 | 0.82601 | 383.4484 | 58.0786 | 15.5295 | 42.5491 | 111.1221 | 85.9 | 4014 | 85 | Note 2 | 8.64 | 221.35 | 33.0981 | 111.1221 | 118231 | 9418.24 | 139390.4 | VPC | 10.5996 | 29.0416 | 1357.0765 | 31.801 | 29.4547 | 2.3463 | 1.2855 | 70
Centerville | GA1530000 | Houston | 11094 | 508.731 | 35.504 | Note 1 | 544.3368 | 320.889 | Note 1 | 12.7 | 0.80222 | 334.3912 | 209.9455 | 11.9216 | 198.0239 | 223.4478 | 53 | 5183 | 65 | 2475754.63 | 3.97 | 396.78 | 25.2477 | 223.4478 | 45925.37 | 78571.93 | 129854.71 | VPC | 6.3018 | 104.6751 | 10236.4391 | 24.0203 | 8.8608 | 15.1595 | 7.8433 | 44
Chatsworth Water Works Commission | GA2130000 | Murray | 30500 | 504.039 | 689.452 | 0.268 | 1193.3434 | 808.959 | Note 1 | 20.616 | 2.0224 | 831.5974 | 361.746 | 12.4243 | 349.3217 | 384.3844 | 431 | 12195 | 90 | 5714807 | 7.95 | 951.27 | 136.6875 | 384.3844 | 97316.07 | 332299.24 | 451150.55 | VPC | 2.7912 | 78.4785 | 2220.5237 | 35.2288 | 7.98 | 27.2488 | 2.5556 | 72
Chattooga County Water District | GA0550000 | Chattoga | 7800 | 360.4731 | 9.9963 | 17.2147 | 353.3864 | 203.9392 | Note 1 | Note 1 | 0.50985 | 204.449 | 148.9374 | 11.7533 | 137.1841 | 149.4472 | 300 | 3527 | 90 | Note 2 | 6.3213 | 581.1374 | 70.6948 | 149.4472 | 74296.02 | 79722.79 | 154315.1 | VPC | 9.1298 | 106.5627 | 1252.8225 | 43.6685 | 21.0649 | 22.6036 | 1.9405 | 51
Cherokee County Water & Sewerage Authority | CS0570002 | Cherokee | 219996 | 7504.2669 | 1.262 | 642.929 | 6855.9798 | 5489.953 | Note 1 | 228.2089 | 5.191 | 5723.3529 | 1132.6268 | 87.4949 | 1045.132 | 1366.0268 | 1382.58 | 78570 | 107 | 45976733 | 6.3 | 283.93 | 752.4046 | 1366.0268 | 534823.64 | 296744.33 | 897837.21 | VPC | 3.0509 | 36.4436 | 2071.0377 | 10.5838 | 6.807 | 3.7768 | 1.3891 | 80
Chickamauga | GA2950000 | Walker | 5720 | 290.054 | 0.053 | Note 1 | 293.0374 | 187.386 | Note 1 | 12.011 | 0.46847 | 199.8655 | 93.1719 | 2.951 | 90.2209 | 105.6514 | 41.9 | 2402 | 145 | 686864.96 | 4.22 | 380 | 31.0659 | 105.6514 | 11987.51 | 34283.93 | 51013.64 | VPC | 3.366 | 102.9061 | 5899.295 | 19.2637 | 4.9906 | 14.2731 | 2.9042 | 52
Clarkesville | GA1370002 | Habersham | 5875 | 236.122 | 0.291 | Note 1 | 238.7981 | 137.798 | Note 1 | 12.226 | 0.34449 | 150.3685 | 88.4296 | 38.195 | 50.2346 | 101.0001 | 61.5 | 2324 | 76.6 | 665879 | 6.33 | 358.62 | 19.0489 | 101.0001 | 223522.76 | 18015.13 | 246045.92 | VPC | 45.0275 | 59.2207 | 2237.87 | 103.932 | 96.1802 | 7.7518 | 2.6371 | 64
Claxton | GA1090001 | Evans | 3840 | 171.581 | Note 1 | Note 1 | 173.5771 | 110.715 | Note 1 | 16.141 | 0.27679 | 127.1328 | 46.4443 | 1.8349 | 44.6094 | 62.8621 | 43 | 1758 | 60 | 1219900 | 4.74 | 451.47 | 10.8696 | 62.8621 | 7998.45 | 20139.81 | 35550.4 | VPC | 2.8596 | 69.5208 | 2842.2683 | 16.0058 | 4.5497 | 11.4561 | 4.104 | 69
Clayton County Water Authority | GA0630000 | Clayton | 296564 | 10228.51 | Note 1 | 101.37 | 10110.8512 | 8752.022 | 0.796 | 0.092 | 50.522 | 8803.432 | 1307.4192 | 30.044 | 1277.3751 | 1358.0332 | 1419 | 89793 | 97.5 | 20171070 | 4.43 | 777.91 | 752.524 | 1358.0332 | 133094.81 | 993682.9 | 1166150.84 | VPC | 0.91669 | 38.9747 | 2466.2847 | 12.5486 | 1.4822 | 11.0664 | 1.6975 | 72
Cleveland Waterworks | GA3110000 | White | 4906 | 171.8147 | 129.985 | 17.038 | 284.6947 | 195.5089 | Note 1 | 0.3825 | 0.48877 | 196.3802 | 88.3145 | 7.036 | 81.2784 | 89.1858 | 50 | 2398 | 90.7 | 1378968.38 | 3.18 | 1727.72 | 20.8631 | 89.1858 | 22357.44 | 140426.39 | 164289.14 | VPC | 8.0387 | 92.861 | 4453.6132 | 67.8832 | 9.3234 | 58.5598 | 3.8958 | 67
Cobb County Water System / Cobb County-Marietta Water Authority | GA0670003/GA0670002 | Cobb | 750000 | 28252.552 | Note 1 | 7043.534 | 21326.2517 | 20317 | Note 1 | Note 1 | 109.876 | 20426.876 | 899.3757 | 224.2228 | 675.1528 | 1009.2517 | 3270 | 198818 | 118 | 175440252 | 5.53 | 2312.36 | 2046.4021 | 1009.2517 | 1239952.23 | 1561196.42 | 3055221.52 | VPC | 3.0898 | 9.3037 | 565.6678 | 14.089 | 6.2366 | 7.8524 | 0.32992 | 75
Cochran | GA0230000 | Bleckley | 6297 | 274.821 | Note 1 | Note 1 | 287.7707 | 146.05 | 9.607 | 2.124 | 0.38914 | 158.1701 | 129.6005 | 6.1525 | 123.4481 | 132.1137 | 64 | 2740 | 53 | Note 2 | 7.18 | 372.67 | 14.6488 | 132.1137 | 43650.33 | 46005.39 | 90592.3 | VPC | 6.1519 | 123.4357 | 5284.5919 | 32.7211 | 15.9308 | 16.7903 | 8.4272 | 61
College Park | GA1210002 | Fulton | 14000 | 171 | 999 | Note 1 | 1157.5818 | 841 | 62 | 75 | 2.2575 | 980.2575 | 177.3243 | 6.8107 | 170.5136 | 254.5818 | 99 | 3272 | 70 | 6439484 | 5.44 | 3858 | 26.2243 | 254.5818 | 36753.05 | 657841.38 | 992653.87 | VPC | 5.7028 | 142.7752 | 4718.7928 | 212.2844 | 11.2326 | 201.0518 | 6.5021 | 54
Columbia County Water Utility | GA0730000 | Columbia | 135000 | 5999.26 | Note 1 | 409.334 | 5586.2877 | 4889.322 | Note 1 | 96.05 | 12.2233 | 4997.5953 | 588.6924 | 45.4735 | 543.2189 | 696.9657 | 892.34 | 53367 | 49.26 | 14279419.76 | 3.78 | 0.3 | 230.729 | 696.9657 | 170763.69 | 543381.84 | 822451.31 | VPC | 2.3345 | 27.8875 | 1667.8294 | 13.3818 | 3.1998 | 10.182 | 2.3544 | 73
Columbus Water Works | GA2150000 | Muscogee | 204366 | 11597.7911 | 4.559 | 1545.5939 | 9422.2444 | 7359.7198 | Note 1 | 593.8262 | 18.3993 | 7971.9454 | 1450.299 | 250.788 | 1199.511 | 2062.5245 | 1222 | 73230 | 91.4 | 23375044.68 | 2.15 | 262.24 | 587.0041 | 2062.5245 | 679068.11 | 314559.75 | 1154177.89 | VPC | 9.3826 | 44.8768 | 2689.3056 | 13.5686 | 9.2731 | 4.2955 | 2.0434 | 75
Commerce | GA1570001 | Jackson | 11000 | 949.11 | 8.4697 | 121.2327 | 836.347 | 535.5019 | Note 1 | Note 1 | 1.3388 | 536.8407 | 299.5063 | 2.6775 | 296.8288 | 300.8451 | 131.05 | 5454 | 66 | Note 2 | 6.75 | 509.57 | 36.7874 | 300.8451 | 18073.19 | 151255.06 | 170010.44 | VPC | 1.345 | 149.107 | 6205.4915 | 31.0466 | 3.3137 | 27.7329 | 8.0688 | 67
Coosa Water Authority | GA2910006 | Union | 5730 | 112.584 | Note 1 | Note 1 | 112.0239 | 89.663 | Note 1 | 1.03 | 0.22416 | 90.9172 | 21.1067 | 0.72121 | 20.3855 | 22.3609 | 185 | 3500 | 152 | 97891.96 | 4.39 | 740.51 | 84.6542 | 22.3609 | 3154.81 | 15095.67 | 19179.2 | VPC | 0.56455 | 15.9573 | 301.8957 | 5.2144 | 0.90138 | 4.313 | 0.24081 | 59
Cordele | GA0810001 | Crisp | 11200 | 633.0509 | Note 1 | Note 1 | 633.0509 | 391.505 | Note 1 | Note 1 | 0.97876 | 392.4838 | 240.5671 | 31.4256 | 209.1415 | 241.5459 | 133 | 6341 | 70 | Note 2 | 3.47 | 278.98 | 42.6859 | 241.5459 | 109046.98 | 58346.29 | 167666.33 | VPC | 13.5779 | 90.3628 | 4308.1985 | 26.3986 | 17.1971 | 9.2014 | 4.8995 | 70
Cornelia | GA1370003 | Habersham | 3700 | 1000.04 | Note 1 | 1.172 | 1029.6908 | 933.11 | Note 1 | 1.45 | 2.3328 | 936.8928 | 92.798 | 4.6656 | 88.1325 | 96.5808 | 70.51 | 2842 | 105 | 5003268 | 4.55 | 464 | 30.9574 | 96.5808 | 21228.25 | 40893.47 | 63876.93 | VPC | 4.4977 | 84.9609 | 3424.4622 | 21.8585 | 7.4695 | 14.389 | 2.8469 | 77
Covington | GA2170001 | Newton | 14391 | Note 1 | 2102.686 | 1005.427 | 1097.9321 | 998.904 | Note 1 | Note 1 | 2.4973 | 1001.4013 | 96.5308 | 15.0845 | 81.4464 | 99.0281 | 188 | 9477 | 90 | 6212043 | 9.95 | 2240 | 80.109 | 99.0281 | 150090.37 | 182439.89 | 338124.13 | VPC | 4.3608 | 23.5455 | 1186.919 | 35.0881 | 15.8373 | 19.2508 | 1.0167 | 69
Coweta County Water & Sewerage Authority | GA0770042 | Coweta | 93891 | 1665.1353 | 1860.8034 | 418.6447 | 3104.3853 | 2545.7791 | Note 1 | 5.297 | 25.95 | 2577.0261 | 527.3592 | 16.5613 | 510.798 | 558.6062 | 1177 | 32822 | 109 | Note 2 | 6.83 | 3705.73 | 449.2073 | 558.6062 | 113088.53 | 1892879.29 | 2121760.8 | VPC | 1.3824 | 42.6375 | 1188.9944 | 61.1166 | 3.4455 | 57.6711 | 1.1371 | 74
Cumming Utilities | GA1170000 | Forsyth | 70047 | 2847.447 | Note 1 | 398.3552 | 2361.4374 | 2210.2222 | Note 1 | 23.7642 | 0.48999 | 2234.4763 | 126.9611 | 58.9711 | 67.9899 | 151.2152 | 411.66 | 23349 | 121.82 | 11594745 | 2.37 | 659.26 | 254.7551 | 151.2152 | 138889.56 | 44823.04 | 199702.41 | VPC | 6.9196 | 7.9778 | 452.4942 | 7.8681 | 5.9484 | 1.9197 | 0.26688 | 71
Cuthbert | GA2430000 | Randolph | 3500 | 252.987 | Note 1 | Note 1 | 252.987 | 97.617 | Note 1 | Note 1 | 0.24404 | 97.861 | 155.126 | 0.48809 | 154.6379 | 155.37 | 20 | 1395 | 45 | 405927.13 | 1.65 | 415.58 | 5.2141 | 155.37 | 805.34 | 64264.41 | 65171.17 | VPC | 0.95858 | 303.7028 | 21183.2702 | 46.645 | 0.5773 | 46.0677 | 29.6575 | 23
Dade County Water & Sewer Authority | GA0830000 | Dade | 16326 | 769.789 | Note 1 | Note 1 | 785.499 | 541.002 | Note 1 | Note 1 | 27.158 | 568.16 | 217.339 | 13.7459 | 203.5931 | 244.497 | 364 | 8673 | 104 | Note 2 | 4.8 | 854.29 | 124.1364 | 244.497 | 65980.16 | 173927.56 | 263108.53 | VPC | 4.3422 | 64.3133 | 1532.3883 | 27.6614 | 7.6075 | 20.0539 | 1.6401 | 74
Dahlonega | GA1870000 | Lumpkin | 7800 | 374.458 | Note 1 | 21.765 | 351.7592 | 251.24 | Note 1 | Note 1 | 0.6281 | 251.8681 | 99.8911 | 3.794 | 96.0971 | 100.5192 | 70.1 | 2689 | 150 | 2186272 | 11.66 | 743.89 | 42.8469 | 100.5192 | 44237.78 | 71485.68 | 116190.7 | VPC | 3.8655 | 97.9099 | 3755.774 | 43.0359 | 16.4514 | 26.5845 | 2.2428 | 68
Dallas | GA2230000 | Paulding | 14000 | 12.301 | 308.43 | Note 1 | 322.1007 | 201.694 | Note 1 | 0.631 | 0.50423 | 202.8292 | 119.2714 | 1.0085 | 118.263 | 120.4067 | 43.5 | 3900 | 108.08 | Note 2 | 9.99 | 5529 | 32.3616 | 120.4067 | 10074.62 | 653875.86 | 670227.19 | VPC | 0.70844 | 83.079 | 7448.4617 | 170.2437 | 2.5832 | 167.6605 | 3.6544 | 85
Dalton Utilities | GA3130000 | Whitfield | 102848 | 8212.326 | 373.9 | 367.97 | 8015.2374 | 5250.58 | 1.2144 | Note 1 | 472.82 | 5724.6144 | 2290.623 | 47.3456 | 2243.2774 | 2763.443 | 1213.69 | 37962 | 110.4 | 26036000 | 5.52 | 1573.87 | 494.0436 | 2763.443 | 261347.92 | 3530626.93 | 4536132.07 | VPC | 3.4169 | 161.8978 | 5063.8675 | 99.8887 | 6.8845 | 93.0042 | 4.5406 | 76
Dawson | GA2730001 | Terrell | 5299 | 412.139 | Note 1 | Note 1 | 549.5187 | 148.023 | Note 1 | Note 1 | 0.37006 | 148.3931 | 401.1256 | 20.9251 | 380.2005 | 401.4957 | 50 | 2535 | 50 | Note 2 | 3.92 | 247.5 | 11.8762 | 401.4957 | 82026.27 | 94099.63 | 176217.5 | VPC | 22.615 | 410.9054 | 20832.9063 | 69.4777 | 32.3575 | 37.1202 | 32.0137 | 50
Dawsonville | GA0850000 | Dawson | 4433 | 126.9328 | Note 1 | Note 1 | 126.9328 | 93.782 | 0.078 | 2.633 | 0.23465 | 96.7277 | 30.2051 | 1.9375 | 28.2676 | 33.0728 | 25.46 | 1754 | 60 | Note 2 | 22.85 | 2052.9159 | 8.7784 | 33.0728 | 43439.11 | 58030.98 | 107357.13 | VPC | 3.0264 | 44.1536 | 3041.8477 | 57.8507 | 24.7657 | 33.0849 | 3.2201 | 71
DeKalb County | GA0890001 | DeKalb | 750000 | 23108.66 | Note 1 | 6.667 | 23101.993 | 22000 | Note 1 | 5.77 | 55 | 22060.77 | 1041.223 | 110 | 931.223 | 1101.993 | 3168 | 245361 | 104 | 72761598.47 | 3.43 | 342.8 | 2047.6774 | 1101.993 | 377300 | 319223.24 | 717355.2 | VPC | 1.2283 | 10.3981 | 805.3333 | 2.8388 | 1.5377 | 1.301 | 0.45477 | 66
Demorest | GA1370004 | Habersham | 18730 | 117.144 | 553.614 | 11.695 | 664.6551 | 468.526 | Note 1 | 3.807 | 6.078 | 478.411 | 186.2441 | 7.1137 | 179.1304 | 196.1291 | 314 | 7149 | 110 | Note 2 | 0.52 | 2198.29 | 111.2593 | 196.1291 | 74515.81 | 393780.55 | 490026.45 | VPC | 2.7262 | 68.6485 | 1562.956 | 65.5052 | 10.4232 | 55.0819 | 1.61 | 68
Douglas | GA0690002 | Coffee | 11727 | 1193.322 | Note 1 | Note 1 | 1205.3758 | 1012.056 | Note 1 | Note 1 | 2.5301 | 1014.5861 | 190.7896 | 5.0603 | 185.7293 | 193.3198 | 125 | 6613 | 65 | 2590954 | 3.9 | 189.69 | 39.578 | 193.3198 | 19735.09 | 35231 | 55446.03 | VPC | 2.0964 | 76.9465 | 4070.78 | 8.3118 | 2.9843 | 5.3275 | 4.6927 | 52
Douglas/Oak Park Subdivision | GA0690002 | Coffee | 11727 | 79.17 | Note 1 | Note 1 | 79.9697 | 56.336 | Note 1 | Note 1 | 0.14084 | 56.4768 | 23.4929 | 0.28168 | 23.2112 | 23.6337 | 12 | 568 | 65 | 111177 | 4.09 | 435.95 | 3.5616 | 23.6337 | 1152.07 | 10118.91 | 11332.38 | VPC | 1.3587 | 111.9582 | 5299.3555 | 19.8433 | 2.0283 | 17.815 | 6.5171 | 52
Douglasville-Douglas County WSA | GA0970000 | Douglas | 147316 | 4718.2 | 0.974 | 56.396 | 4691.687 | 3934.0355 | Note 1 | 3.3285 | 11.7587 | 3949.1227 | 742.5643 | 79.63 | 662.9343 | 757.6515 | 966.88 | 46427 | 98 | 21629371 | 6.93 | 422.42 | 436.2105 | 757.6515 | 551506.29 | 280036.7 | 837916.12 | VPC | 4.6991 | 39.1207 | 1878.4733 | 17.9108 | 11.879 | 6.0318 | 1.5198 | 81
Dublin | GA1750002 | Laurens | 21362 | 1107.57 | Note 1 | Note 1 | 1107.57 | 742.918 | Note 1 | 27.608 | 1.8573 | 772.3833 | 335.1867 | 61.7112 | 273.4755 | 364.652 | 227 | 8237 | 62 | Note 2 | 5.28 | 407.35 | 55.7517 | 364.652 | 315709.51 | 111400.26 | 439112.46 | VPC | 20.5259 | 90.9613 | 3300.6522 | 51.8526 | 38.3282 | 13.5244 | 4.9052 | 54
East Dublin | GA1750004 | Laurens | 4087 | 128.3 | Note 1 | Note 1 | 129.596 | 90.528 | Note 1 | Note 1 | 0.22632 | 90.7543 | 38.8416 | 2.3002 | 36.5415 | 39.068 | 40 | 1460 | 65 | Note 2 | 3.59 | 657.37 | 10.3299 | 39.068 | 8257.54 | 24021.28 | 32427.59 | VPC | 4.3163 | 68.571 | 2502.8417 | 22.1088 | 5.6558 | 16.4529 | 3.5375 | 65
East Point Water Treatment Plant | GA1210003 | Fulton | 33712 | 3453.5 | Note 1 | 852.979 | 2610.4974 | 2589.305 | Note 1 | Note 1 | 6.4733 | 2595.7783 | 14.7191 | 12.9465 | 1.7726 | 21.1924 | 194 | 11303 | 74 | Note 2 | 3.91 | 241.58 | 74.1422 | 21.1924 | 50620.91 | 428.22 | 52612.94 | VPC | 3.1381 | 0.42965 | 25.0328 | 4.5164 | 4.4785 | 0.037885 | 0.023908 | 67
Eastman | GA0910002 | Dodge | 5595 | 397.086 | Note 1 | Note 1 | 399.6035 | 226.636 | Note 1 | 11.256 | 0.56659 | 238.4586 | 161.1449 | 1.7294 | 159.4155 | 172.9675 | 65 | 3533 | 61 | 1927076.93 | 5.82 | 383.9 | 19.6288 | 172.9675 | 9911.76 | 61199.61 | 75650.06 | VPC | 1.3411 | 123.6215 | 6719.305 | 20.1278 | 2.8055 | 17.3223 | 8.1215 | 53
Eatonton-Putnam Water & Sewer Authority | GA2370000 | Putnam | 11479 | Note 1 | 473.509 | 10.196 | 463.313 | 366.367 | Note 1 | 8.575 | 0.91592 | 375.8579 | 87.4551 | 9.4837 | 77.9714 | 96.946 | 244 | 14849 | 78 | 3549835 | 3.8 | 473.51 | 100.9942 | 96.946 | 35455.97 | 36920.22 | 76870.24 | VPC | 1.7498 | 14.3862 | 875.4926 | 4.8741 | 2.3878 | 2.4864 | 0.77204 | 78
Effingham County Surface Water System | CP1030131 | Effingham | 9869 | Note 1 | 1007.047 | Note 1 | 1007.047 | 928.159 | Note 1 | 63.175 | 2.3204 | 993.6544 | 13.3926 | 4.6408 | 8.7518 | 78.888 | 113.52 | 4017 | 55 | 1748780 | 1.84 | 667.15 | 24.4251 | 78.888 | 8539.06 | 5838.77 | 58073.09 | VPC | 3.1652 | 5.969 | 211.2188 | 3.5792 | 2.1257 | 1.4535 | 0.35831 | 49
Elberton | GA1050001 | Elbert | 9000 | 706.463 | Note 1 | 125.134 | 595.625 | 504.446 | 0.582 | 7.218 | 1.2626 | 513.5086 | 82.1165 | -4.2229 | 86.3393 | 90.597 | 129.2 | 4015 | 74 | 1492541 | 3.87 | 537.89 | 35.146 | 90.597 | 35569.86 | 46441.06 | 86572.53 | VPC | -2.8816 | 58.9156 | 1830.8522 | 20.4261 | 8.8592 | 11.5669 | 2.4566 | 62
Ellijay Gilmer County Water and Sewer Auth | GA1230000 | Gilmer | 16688 | 1070 | Note 1 | 74 | 997.8257 | 845 | Note 1 | 58 | 2.1125 | 905.1125 | 92.7132 | 6.6334 | 86.0798 | 152.8257 | 249 | 7130 | 93.8 | 3180174 | 4.97 | 698.97 | 82.7368 | 152.8257 | 32307.24 | 60167.23 | 134491.3 | VPC | 2.5489 | 33.0765 | 947.1292 | 12.9698 | 4.5312 | 8.4386 | 1.0404 | 81
Etowah Water & Sewer Authority | GA0850007 | Dawson | 21011 | 674.88 | 1.661 | Note 1 | 678.5739 | 526.04 | Note 1 | 5.307 | 39.607 | 570.954 | 107.6199 | 12.2789 | 95.341 | 152.5339 | 220.66 | 7782 | 99 | 4170377.56 | 14.28 | 371.82 | 85.3173 | 152.5339 | 173836.58 | 35449.68 | 225986.19 | VPC | 4.3229 | 33.5657 | 1183.7585 | 26.8936 | 22.3383 | 4.5553 | 1.1175 | 77
Fairburn | GA1210004 | Fulton | 17632 | Note 1 | 515.731 | Note 1 | 510.6248 | 375.78 | Note 1 | Note 1 | 0.93945 | 376.7194 | 133.9053 | 5.6747 | 128.2306 | 134.8448 | 86 | 7270 | 75 | 3605000 | 8.62 | 4950 | 42.5889 | 134.8448 | 48915.55 | 634741.69 | 688307.52 | VPC | 2.1385 | 48.3242 | 4085.0795 | 94.0381 | 6.7284 | 87.3097 | 3.0109 | 66
Fayette County Water System | GA1130001 | Fayette | 77051 | 3537.1935 | 0.90059 | 227.049 | 3392.2385 | 2964.0897 | 0.491 | 2.173 | 7.4115 | 2974.1651 | 418.0734 | 75.3589 | 342.7145 | 427.6579 | 721.5436 | 33268.25 | 86.98 | 16447171 | 6.6451 | 653.9424 | 282.3573 | 427.6579 | 500499.78 | 224115.57 | 730883.03 | VPC | 6.206 | 28.2234 | 1301.299 | 21.781 | 15.0444 | 6.7366 | 1.2138 | 72
Fayettville | GA1130003 | Fayettville | 18645 | 308.18 | 307.888 | Note 1 | 616.4692 | 476.7367 | Note 1 | Note 1 | 1.1918 | 477.9285 | 138.5407 | 7.1992 | 131.3415 | 139.7325 | 105 | 7932 | 60 | Note 2 | 4.07 | 1361.29 | 38.4969 | 139.7325 | 29300.76 | 178793.81 | 209717.02 | VPC | 2.4866 | 45.3656 | 3427.0439 | 26.2348 | 3.694 | 22.5408 | 3.4117 | 68
Fitzgerald Utilities | CG0170000 | Ben Hill | 9050 | 805.659 | Note 1 | Note 1 | 830.5763 | 681.655 | Note 1 | 94.072 | 1.7041 | 777.4311 | 53.1452 | 3.4083 | 49.7369 | 148.9213 | 135 | 6101 | 59.46 | 1406467.26 | 2.1 | 129.43 | 35.7121 | 148.9213 | 7157.38 | 6437.44 | 25991.13 | VPC | 1.5305 | 22.3349 | 1009.3734 | 2.2283 | 1.1731 | 1.0551 | 1.3927 | 71
Flowery Branch | GA1390000 | Towns | 4594 | 130.325 | 4.415 | Note 1 | 134.74 | 123.284 | Note 1 | Note 1 | 0.30821 | 123.5922 | 11.1478 | 4.6919 | 6.4559 | 11.456 | 21 | 8455 | 80 | Note 2 | 7.39 | 1142.61 | 40.3503 | 11.456 | 46351.49 | 7376.54 | 54080.19 | VPC | 1.5204 | 2.0919 | 842.2526 | 6.3546 | 5.4821 | 0.87245 | 0.16 | 52
Floyd County Water | GA1150001 | Floyd | 100387 | 1464.148 | 516.4357 | 86.062 | 1933.1854 | 1529.079 | Note 1 | 1.0794 | 3.8227 | 1533.9811 | 399.2043 | 23.1015 | 376.1028 | 404.1064 | 594 | 19461 | 90 | Note 2 | 4.88 | 925.86 | 201.4589 | 404.1064 | 112692.41 | 348218.51 | 465449.58 | VPC | 3.2522 | 52.9479 | 1734.7114 | 23.6838 | 5.7907 | 17.8931 | 1.8669 | 78
Folkston | GA0490000 | Charlton | 3300 | 177.241 | Note 1 | 1.7 | 175.5131 | 145.105 | Note 1 | 0.178 | 0.36276 | 145.6458 | 29.8673 | 2.193 | 27.6743 | 30.4081 | 61.2 | 2412 | 52 | 759319.58 | 3.09 | 233.42 | 13.1511 | 30.4081 | 6771.33 | 6459.73 | 13357.29 | VPC | 2.491 | 31.4345 | 1238.8886 | 5.4855 | 2.8073 | 2.6782 | 2.1043 | 48
Forsyth | GA2070001 | Monroe | 9066 | 564.72 | 0.555 | 18.756 | 545.6055 | 518.968 | Note 1 | Note 1 | 1.4 | 520.368 | 25.2375 | 1.5073 | 23.7302 | 26.6375 | 52 | 3487 | 70 | 1693889 | 8.11 | 549.84 | 20.5517 | 26.6375 | 12224.13 | 13047.8 | 26041.71 | VPC | 1.1843 | 18.6447 | 1250.2732 | 7.2475 | 3.5056 | 3.7418 | 1.1547 | 72
Forsyth County Dept. of Water and Sewer | GA1170050 | Forsyth | 199000 | 5373.87 | 380.153 | 46.17 | 5707.8177 | 5091.918 | Note 1 | 15.404 | 12.7298 | 5120.0518 | 587.7659 | 129.6907 | 458.0752 | 615.8997 | 1135.3 | 67875 | 116.6 | 48131678.13 | 11.58 | 1432.29 | 694.7 | 615.8997 | 1498627.63 | 656096.58 | 2195019.97 | VPC | 5.2349 | 18.4899 | 1105.4353 | 31.7455 | 22.0792 | 9.6662 | 0.65939 | 72
Fort Oglethorpe | Ga0470001 | Catoosa | 10531 | Note 1 | 239.987 | Note 1 | 239.987 | 188.062 | Note 1 | Note 1 | 0.47016 | 188.5322 | 51.4548 | 0.94031 | 50.5145 | 51.925 | 38 | 3057 | 110 | 1491244 | 0.1 | 2250.3 | 26.6648 | 51.925 | 9497.13 | 113672.86 | 124227.98 | VPC | 0.84272 | 45.2718 | 3641.9996 | 40.2911 | 3.1067 | 37.1844 | 1.8944 | 41
Fort Valley Utility Commission | GA2250001 | Peach | 14035 | 796.259 | Note 1 | Note 1 | 804.302 | 483.594 | Note 1 | Note 1 | 1.209 | 484.803 | 319.499 | 17.3745 | 302.1245 | 320.708 | 158 | 5614 | 57 | 3058830 | 4.73 | 369.987 | 35.3036 | 320.708 | 109860.44 | 111782.16 | 222089.91 | VPC | 8.479 | 147.4418 | 5238.8512 | 39.4803 | 19.569 | 19.9113 | 8.5579 | 46
Franklin County Water | GA1190051 | Flanklin | 5691 | 476.5204 | 341.7203 | 217.8995 | 600.2698 | 466.2274 | Note 1 | 6.2636 | 1.1656 | 473.6566 | 126.6132 | 16.9443 | 109.669 | 134.0425 | 244 | 2566 | 125 | 2888396 | 5.5272 | 2607.5493 | 77.7879 | 134.0425 | 93088.85 | 285967.27 | 398428.16 | VPC | 18.0914 | 117.0939 | 1231.4056 | 147.7226 | 36.2778 | 111.4448 | 1.4098 | 61
Gainesville | GA1390001 | Hall | 197777 | 7619.355 | Note 1 | Note 1 | 7529.6021 | 6866 | Note 1 | 6.098 | 205.0234 | 7077.1214 | 452.4807 | 268.0429 | 184.4379 | 663.6021 | 1474 | 63800 | 123 | 36008710 | 6.53 | 443 | 787.6531 | 663.6021 | 1749152.22 | 81705.98 | 1924384.98 | VPC | 11.5104 | 7.9202 | 342.8149 | 28.6968 | 27.4162 | 1.2807 | 0.23416 | 77
Garden City | GA0510000 | Chatham | 10306 | 400.128 | Note 1 | Note 1 | 386.338 | 263.863 | Note 1 | 19.107 | 0.457 | 283.427 | 102.911 | 7.0942 | 95.8168 | 122.475 | 51 | 3616 | 52 | Note 2 | 2.62 | 199.75 | 15.5315 | 122.475 | 17643.09 | 19139.4 | 40690.4 | VPC | 5.3751 | 72.5973 | 5147.2891 | 10.1721 | 4.8792 | 5.293 | 6.1692 | 48
Glen of Robin Hood | GA0510109 | Chatham | 6575 | 140 | Note 1 | Note 1 | 140 | 127.534 | Note 1 | Note 1 | 0.31884 | 127.8528 | 12.1472 | 0.63767 | 11.5095 | 12.466 | 37 | 2435 | 45 | Note 2 | 2.33 | 384.62 | 9.287 | 12.466 | 1485.77 | 4426.78 | 6035.18 | VPC | 0.71747 | 12.9498 | 852.2395 | 2.4282 | 0.61017 | 1.818 | 1.2393 | 56
Glennville | CG2670002 | Tattnal | 5289 | 246.934 | Note 1 | Note 1 | 246.934 | 183.149 | Note 1 | 4.308 | 0.45787 | 187.9149 | 59.0191 | 2.8093 | 56.2099 | 63.785 | 52 | 2129 | 46.8 | Note 2 | 4.28 | 275.58 | 10.2606 | 63.785 | 11849.34 | 15490.32 | 28653.03 | VPC | 3.6151 | 72.3343 | 2961.532 | 12.8415 | 5.5657 | 7.2759 | 5.4782 | 73
Gray | GA1690000 | Jones | 9191 | 106.653 | 108.348 | 3.424 | 213.7314 | 175.9 | Note 1 | 1.712 | 0.43975 | 178.0517 | 35.6796 | 3.5843 | 32.0954 | 37.8314 | 60.6 | 2120 | 60 | 800000 | 6.91 | 2596.38 | 14.144 | 37.8314 | 24654.72 | 83331.82 | 113573.29 | VPC | 4.632 | 41.4776 | 1451.0324 | 50.937 | 11.6296 | 39.3075 | 2.2692 | 55
Grovetown | GA0730001 | Columbia | 14053 | Note 1 | 395.844 | Note 1 | 405.3702 | 358.691 | Note 1 | Note 1 | 0.89673 | 359.5877 | 45.7825 | 5.4166 | 40.3659 | 46.6792 | 69.2 | 5790 | 80 | 6089926.96 | 0.25 | 853.57 | 36.2919 | 46.6792 | 55520.11 | 34455.1 | 90740.63 | VPC | 2.563 | 19.1004 | 1598.1422 | 15.5398 | 9.589 | 5.9508 | 1.1123 | 55
Gwinnett County DWR | GA1350004 | Gwinnett | 1099323 | 28872.2433 | Note 1 | 114.838 | 28097.3803 | 25570.4328 | Note 1 | 1.1387 | 8.293 | 25579.8645 | 2517.5158 | 568.17 | 1949.3458 | 2526.9475 | 4056.13 | 289582 | 109.4 | 31291918 | 6.09 | 333.45 | 2610.7272 | 2526.9475 | 3460026.42 | 650009.34 | 4113180.76 | VPC | 5.3754 | 18.4427 | 1316.6918 | 14.193 | 11.9483 | 2.2446 | 0.74667 | 81
Hahira | CG1850000 | Lowndes | 3440 | 110.047 | Note 1 | Note 1 | 115.8389 | 100.858 | Note 1 | 2.178 | 0.25215 | 103.2881 | 12.5508 | 1.5451 | 11.0057 | 14.9809 | 25 | 2961 | 60 | 468353 | 6.1 | 548.01 | 12.6889 | 14.9809 | 9302.71 | 6031.26 | 16665.71 | VPC | 1.4296 | 10.1833 | 1206.109 | 5.1786 | 3.1417 | 2.0369 | 0.86735 | 64
Hampton | GA1510000 | Henry | 7305 | 14.0345 | 246.2938 | Note 1 | 261.5162 | 192.3157 | Note 1 | Note 1 | 0.48079 | 192.7965 | 68.7197 | 11.0835 | 57.6362 | 69.2005 | 42.5 | 3343 | 56 | Note 2 | 12.1048 | 4229.0117 | 14.9493 | 69.2005 | 134163.35 | 243744.24 | 379940.85 | VPC | 9.0834 | 47.2353 | 3715.4693 | 113.0444 | 40.1326 | 72.9118 | 3.8554 | 63
Hapeville | GA1210006 | Fulton | 6500 | Note 1 | 328.555 | Note 1 | 330.6047 | 271.678 | Note 1 | 2.1436 | 0.67919 | 274.5008 | 56.104 | 2.0447 | 54.0593 | 58.9267 | 41 | 2513 | 75 | 3777292 | 13.52 | 5303.99 | 16.3911 | 58.9267 | 27599.66 | 286730.05 | 329301.69 | VPC | 2.2291 | 58.9366 | 3612.383 | 125.0815 | 10.9828 | 114.0987 | 3.2981 | 65
Haralson County Water Authority | GA1430007 | Haralson | 15000 | 936.184 | 76.217 | 551.896 | 469.9031 | 301.877 | Note 1 | 0.676 | 0.75469 | 303.3077 | 166.5954 | 1.5699 | 165.0255 | 168.0261 | 263.8 | 6224 | 92.01 | 3356987 | 7.03 | 501.85 | 79.2829 | 168.0261 | 11035.57 | 82818.03 | 94571.59 | VPC | 0.69105 | 72.6421 | 1713.8914 | 15.0793 | 1.7731 | 13.3062 | 2.0815 | 71
Harris County Waterworks | GA1450011 | Harris | 24310 | 701.64 | 304.1291 | 1.5256 | 1009.1866 | 919.2645 | Note 1 | 0.3867 | 2.2982 | 921.9494 | 87.2372 | 28.1771 | 59.0601 | 89.9221 | 525 | 9589 | 90.1761 | 6862056.94 | 5.8133 | 1727.6775 | 140.8271 | 89.9221 | 163762.02 | 102036.83 | 270437.42 | VPC | 8.0506 | 16.8744 | 308.2067 | 27.7191 | 17.0781 | 10.641 | 0.41938 | 54
Hart County Water and Sewer Authority | GA1470065 | Hart | 8399 | Note 1 | 372.91 | 23.087 | 351.8357 | 324.97 | Note 1 | 2.849 | 0.81243 | 328.6314 | 23.2043 | 2.3147 | 20.8896 | 26.8657 | 182.7 | 3206 | 95 | Note 2 | 4.73 | 2344.64 | 50.9482 | 26.8657 | 10934.32 | 48978.6 | 68497.64 | VPC | 1.9781 | 17.8515 | 313.2556 | 18.6877 | 3.4106 | 15.2772 | 0.41002 | 60
Hartwell | GA1470000 | Hart | 8386 | 654.397 | Note 1 | 205.44 | 445.7013 | 380.498 | Note 1 | 18.019 | 3.383 | 401.9 | 43.8013 | 1.9025 | 41.8988 | 65.2033 | 90.076 | 3394 | 88.8 | Note 2 | 5.1954 | 361.456 | 32.2957 | 65.2033 | 9884.2 | 15144.57 | 32764.65 | VPC | 1.5357 | 33.8218 | 1274.3821 | 7.3744 | 2.9123 | 4.4622 | 1.2974 | 66
Hawkinsville | GA2350001 | Pulaski | 7491 | 284.122 | Note 1 | Note 1 | 284.122 | 202.171 | Note 1 | 7.914 | 7.103 | 217.188 | 66.934 | 1.0109 | 65.9231 | 81.951 | 60 | 1930 | 55 | 650000 | 4.1 | 437 | 12.3281 | 81.951 | 4144.51 | 28808.41 | 39515.35 | VPC | 1.435 | 93.581 | 3010.1893 | 17.0741 | 2.1474 | 14.9266 | 5.3474 | 52
Hazlehurst | GA1610001 | Jeff Davis | 12409 | 310.632 | Note 1 | Note 1 | 326.2941 | 181.461 | 8.923 | 4.586 | 0.47596 | 195.446 | 130.8482 | 10.7439 | 120.1043 | 135.9101 | 78 | 3097 | 51 | Note 2 | 2.68 | 294.6 | 16.5028 | 135.9101 | 28217.8 | 35382.72 | 65091.78 | VPC | 9.5044 | 106.2489 | 4218.6263 | 20.5362 | 9.1113 | 11.4248 | 7.2778 | 71
Heard County Water Authority | GA1490000 | Heard | 8172 | 582.83 | 5.6275 | 1.4825 | 581.2802 | 290.53 | Note 1 | 8.9713 | 0.72632 | 300.2276 | 281.0526 | 17.2159 | 263.8367 | 290.7502 | 300 | 3983 | 80 | Note 2 | 0.01 | 842.8975 | 64.8371 | 290.7502 | 168002.46 | 222387.34 | 398563.87 | VPC | 11.842 | 181.4814 | 2409.4679 | 98.014 | 42.1799 | 55.8341 | 4.0692 | 67
Henry County Water Authority | GA1510001 | Henry | 255000 | 6652.964 | 1.8305 | 737.656 | 5944.4138 | 5283.0897 | Note 1 | 130.7804 | 15.5979 | 5429.468 | 514.9458 | 57.8232 | 457.1226 | 661.324 | 1384.07 | 74141 | 99 | 42634453 | 9.0151 | 470.34 | 672.4351 | 661.324 | 512619.63 | 215003.04 | 796470.21 | VPC | 2.1367 | 16.892 | 904.8608 | 9.814 | 6.9141 | 2.8999 | 0.6798 | 96
Hephzibah Waterworks | GA2450002 | Richmond | 4011 | 208.835 | Note 1 | Note 1 | 208.835 | 142.5277 | Note 1 | 0.7918 | 0.35632 | 143.6758 | 65.1592 | 6.2965 | 58.8627 | 66.3073 | 50.4 | 1820 | 70 | Note 2 | 3.6787 | 816.5467 | 13.9417 | 66.3073 | 23074.92 | 48064.12 | 72076.53 | VPC | 9.4784 | 88.6086 | 3199.7538 | 39.0874 | 12.6785 | 26.4089 | 4.2221 | 64
Hiawassee | GA1370004 | Towns | 6317 | 516.41 | Note 1 | 275.641 | 242.1403 | 115.581 | Note 1 | 0.493 | 0.28895 | 116.363 | 125.7774 | 2.9468 | 122.8306 | 126.5593 | 75.4 | 2411 | 95 | Note 2 | 12.8 | 890.54 | 26.6846 | 126.5593 | 37598.73 | 109385.59 | 147680.68 | VPC | 3.3485 | 139.5779 | 4463.1603 | 60.964 | 15.5947 | 45.3694 | 4.603 | 71
Hinesville | GA1790000 | Liberty | 28099 | 1255.308 | Note 1 | Note 1 | 1267.9879 | 1127.1113 | 0.549 | 19.1925 | 2.8192 | 1149.672 | 118.3159 | 8.5112 | 109.8047 | 140.3276 | 215.92 | 15071 | 50 | 2633981 | 4.94 | 162.04 | 62.5752 | 140.3276 | 41815.72 | 17792.75 | 63175.23 | VPC | 1.5472 | 19.9612 | 1393.2695 | 3.9552 | 2.7746 | 1.1806 | 1.7548 | 70
Homerville | GA0650000 | Clinch | 3210 | 152.173 | Note 1 | Note 1 | 152.173 | 80.382 | Note 1 | 16.575 | 0.20096 | 97.158 | 55.015 | 0.40191 | 54.6131 | 71.791 | 45 | 1368 | 45 | 393224 | 2.5 | 3.34 | 7.3691 | 71.791 | 1004.78 | 182.41 | 1243.21 | VPC | 0.80491 | 109.375 | 3325.0006 | 0.86782 | 0.73448 | 0.13334 | 7.4111 | 43
Hoschton | GA1570002 | Jackson | 6678 | 45.357 | 118.47 | Note 1 | 164.2927 | 113.531 | Note 1 | 0.526 | 0.28383 | 114.3408 | 49.9519 | 2.8953 | 47.0566 | 50.7617 | 31.3 | 2549 | 41 | Note 2 | 13.06 | 2547.09 | 8.2559 | 50.7617 | 37700.4 | 119857.3 | 159620.41 | VPC | 3.112 | 50.5775 | 4118.9166 | 61.8116 | 14.7903 | 47.0213 | 5.6997 | 68
Houston County - Feagin Mill System | GA1530021 | Houston | 163000 | 6031.915 | Note 1 | 2154.237 | 3719.1804 | 2669.1329 | Note 1 | Note 1 | 11.5357 | 2680.6685 | 1038.5119 | 40.3066 | 998.2053 | 1050.0476 | 436 | 20068 | 65 | Note 2 | 2.04 | 312.41 | 127.3786 | 1050.0476 | 82225.47 | 311849.32 | 397678.65 | VPC | 5.5027 | 136.2771 | 6272.4979 | 19.637 | 4.0973 | 15.5396 | 7.8365 | 60
Jackson County Water and Sewerage Utility | GA1570117 | Jackson | 36367 | Note 1 | 1659.96 | 531.42 | 1125.7085 | 776.07 | Note 1 | 284.46 | 1.9402 | 1062.4702 | 63.2383 | 13.1879 | 50.0504 | 349.6385 | 446.22 | 12276 | 102 | 12090302 | 9.14 | 2359.71 | 158.4304 | 349.6385 | 103610.6 | 118104.32 | 897536.28 | VPC | 2.9432 | 11.1701 | 307.3019 | 18.0608 | 8.4401 | 9.6207 | 0.31591 | 64
Jasper | GA2270000 | Pickens | 14435 | 512.28 | 260.747 | 16.116 | 771.6138 | 433.947 | Note 1 | 8.218 | 1.0849 | 443.2499 | 328.364 | 6.636 | 321.7279 | 337.6668 | 200 | 6870 | 70 | 4477923 | 3.14 | 1787.79 | 53.9744 | 337.6668 | 20724.94 | 575181.93 | 612538.45 | VPC | 2.6464 | 128.3037 | 4407.2316 | 86.7404 | 3.0167 | 83.7237 | 5.9608 | 69
Jefferson | GA1570003 | Jackson | 12355 | 570.769 | 79.258 | Note 1 | 648.1774 | 505.523 | 0.076 | 22.582 | 8.295 | 536.476 | 111.7014 | 10.5702 | 101.1312 | 142.5784 | 131.83 | 5863 | 85 | Note 2 | 6.11 | 1091.05 | 49.412 | 142.5784 | 62857.98 | 110339.2 | 206885.53 | VPC | 4.9394 | 47.2577 | 2101.7355 | 29.5407 | 10.7211 | 18.8196 | 2.0467 | 70
Jesup | GA3050000 | Wayne | 9899 | 460.624 | Note 1 | Note 1 | 464.589 | 398.33 | Note 1 | 4.389 | 0.99582 | 403.7148 | 60.8742 | 10.2104 | 50.6638 | 66.259 | 136 | 4085 | 57 | Note 2 | 3.86 | 309.38 | 28.0558 | 66.259 | 39094.13 | 15674.36 | 56434.44 | VPC | 6.8479 | 33.9792 | 1020.6239 | 13.4072 | 9.5702 | 3.8371 | 1.8058 | 74
Jones County Water Systems | GA1690002 | Jones | 12480 | 610.407 | Note 1 | 108.689 | 517.2351 | 289.083 | Note 1 | Note 1 | 7.939 | 297.022 | 220.2131 | 16.6603 | 203.5528 | 228.1521 | 200 | 4800 | 77 | Note 2 | 4.44 | 868.52 | 50.6452 | 228.1521 | 73971.78 | 176789.66 | 257656.62 | VPC | 9.5093 | 116.1831 | 2788.3943 | 52.242 | 15.4108 | 36.8312 | 4.0192 | 82
Kingsland | GA0390000 | Camden | 32000 | 710.339 | Note 1 | Note 1 | 728.5528 | 649.765 | Note 1 | 0.844 | 1.6244 | 652.2334 | 76.3194 | 4.8794 | 71.44 | 78.7878 | 191.6 | 9010 | 65 | 1709361 | 2.27 | 241.24 | 56.6566 | 78.7878 | 11072 | 17234.18 | 28901.66 | VPC | 1.4837 | 21.7232 | 1021.5344 | 3.1416 | 1.2289 | 1.9128 | 1.2609 | 79
Lafayette | GA2950002 | Walker | 16000 | 704.858 | 482.937 | Note 1 | 1169.1927 | 656.422 | Note 1 | 27.7 | 1.6411 | 685.7631 | 483.4296 | 39.2885 | 444.1411 | 512.7707 | 638 | 8293 | 75 | Note 2 | 3.44 | 784.06 | 128.5401 | 512.7707 | 131280.47 | 348233.28 | 502518.9 | VPC | 12.9796 | 146.7292 | 1907.2492 | 57.8215 | 15.8303 | 41.9912 | 3.4553 | 70
LaGrange | GA2850001 | Troup | 46252 | 2539.34 | Note 1 | 159.0042 | 2380.3358 | 2025.729 | Note 1 | Note 1 | 5.0643 | 2030.7933 | 349.5425 | 10.1286 | 339.4138 | 354.6068 | 470.09 | 22610 | 81 | Note 2 | 5.65 | 548.02 | 175.459 | 354.6068 | 57226.84 | 186005.57 | 246007.76 | VPC | 1.2273 | 41.1279 | 1978.1338 | 10.7577 | 2.531 | 8.2267 | 1.9344 | 71
Lake Blackshear Area Water System | GA0810064 | Crisp | 3978 | 91.645 | Note 1 | Note 1 | 91.645 | 83.009 | Note 1 | 4.273 | 0.20752 | 87.4895 | 4.1555 | 0.41504 | 3.7404 | 8.636 | 116 | 1515 | 62 | 647866 | 3 | 296.46 | 19.3444 | 8.636 | 1245.14 | 1108.89 | 3682.32 | VPC | 0.75057 | 6.7642 | 88.3428 | 1.5538 | 0.82187 | 0.73194 | 0.19336 | 79
Larchmont/Consolidated Utilities | GA0510034 | Chatham | 16339 | 621.3 | Note 1 | Note 1 | 621.3 | 359.1 | Note 1 | 9.4 | 0.89775 | 369.3977 | 251.9022 | 42.7399 | 209.1623 | 262.2 | 64 | 6227 | 49 | 2500000 | 6.9 | 189.11 | 22.898 | 262.2 | 287896.46 | 39554.68 | 329398.56 | VPC | 18.8045 | 92.0262 | 8953.8658 | 52.5857 | 46.2336 | 6.3521 | 9.1345 | 58
Lavonia | GA1190003 | Franklin | 8190 | 463.063 | 23.087 | 143.217 | 342.3863 | 227.504 | Note 1 | 44.88 | 0.56876 | 272.9528 | 69.4335 | 3.8889 | 65.5446 | 114.8823 | 129 | 3953 | 107 | 1810891 | 6.62 | 609.64 | 50.4138 | 114.8823 | 23019.65 | 39958.64 | 90685.66 | VPC | 2.6953 | 45.4274 | 1392.0493 | 15.9318 | 5.8233 | 10.1084 | 1.3001 | 52
Lee County Utilities Authority | GA1770068 | Lee | 18468 | 627.485 | Note 1 | Note 1 | 645.9594 | 555.231 | Note 1 | 2.176 | 1.3881 | 558.7951 | 87.1644 | 14.1518 | 73.0126 | 90.7284 | 89 | 6855 | 68 | Note 2 | 2.25 | 306.33 | 37.4717 | 90.7284 | 31755.25 | 22365.94 | 55212.97 | VPC | 5.656 | 29.1808 | 2247.5775 | 7.8951 | 4.6324 | 3.2627 | 1.9485 | 67
Leesburg | GA1770000 | Lee | 3400 | 150.406 | Note 1 | Note 1 | 150.406 | 120.888 | Note 1 | 25.764 | 1.155 | 147.807 | 2.599 | 0.60444 | 1.9946 | 29.518 | 25.3 | 1645 | 62 | Note 2 | 3.5 | 183.59 | 8.6814 | 29.518 | 2115.54 | 366.18 | 7423.78 | VPC | 1.0067 | 3.3219 | 215.99 | 1.5086 | 1.286 | 0.2226 | 0.22975 | 87
Lincoln County Board of Commissioners | GA1810038 | Lincoln | 6329 | 32.611 | 76.138 | Note 1 | 109.2544 | 75.007 | Note 1 | Note 1 | 0.18752 | 75.1945 | 34.0598 | 1.5173 | 32.5426 | 34.2474 | 140.7 | 2416 | 69 | Note 2 | 14.45 | 1995.47 | 28.2975 | 34.2474 | 21924.6 | 64937.71 | 87236.5 | VPC | 1.7206 | 36.903 | 633.6724 | 35.9529 | 9.0748 | 26.8782 | 1.15 | 63
Loganville | CP1350006 | Walton | 12319 | Note 1 | 463.397 | Note 1 | 463.397 | 341.456 | Note 1 | 16.152 | 0.85364 | 358.4616 | 104.9354 | 5.3195 | 99.6159 | 121.941 | 88 | 6579 | 80 | Note 2 | 6.67 | 3589.2 | 42.7176 | 121.941 | 34978.31 | 357541.31 | 453556.26 | VPC | 2.2152 | 41.4835 | 3101.3661 | 59.6625 | 5.3167 | 54.3458 | 2.332 | 76
Lowndes Co.-North Lowndes Co. WS | GA1850016 | Lowndes | 13814 | 586.182 | Note 1 | Note 1 | 586.182 | 508.13 | 0.667 | Note 1 | 1.272 | 510.069 | 76.113 | 2.544 | 73.569 | 77.385 | 120 | 6301 | 61 | 3205292 | 6.23 | 182.87 | 35.4982 | 77.385 | 15849.03 | 13453.57 | 29535.2 | VPC | 1.1061 | 31.9884 | 1679.658 | 4.6505 | 2.5153 | 2.1351 | 2.0725 | 58
Lowndes Co.-South Lowndes Co. WS | GA1850019 | Lowndes | 8546 | 451.523 | Note 1 | Note 1 | 451.523 | 315.731 | 0.036 | 6.031 | 0.78942 | 322.5874 | 128.9356 | 1.5788 | 127.3567 | 135.756 | 92 | 3710 | 61 | 1989492 | 6.23 | 227 | 23.4722 | 135.756 | 9836.14 | 28909.98 | 40294.36 | VPC | 1.1659 | 94.0492 | 3792.6369 | 10.4437 | 2.6513 | 7.7924 | 5.4259 | 58
Lyons | GA2790000 | Toombs | 4100 | 382.171 | Note 1 | Note 1 | 394.3973 | 219.724 | 0.859 | 49.901 | 0.55146 | 271.0355 | 123.3619 | 9.4418 | 113.92 | 173.8143 | 42 | 2802 | 58 | 361629.41 | 3.004 | 168.23 | 13.708 | 173.8143 | 23986.74 | 19164.77 | 51639.12 | VPC | 9.232 | 111.3882 | 7431.1824 | 15.4003 | 8.5606 | 6.8397 | 8.3105 | 69
Macon Water Authority | GA0210001 | Bibb | 135000 | 9652.46 | Note 1 | 323.01 | 8798.5647 | 7504.09 | Note 1 | 386.61 | 45.62 | 7936.32 | 862.2447 | 165.0898 | 697.1549 | 1294.4747 | 1419.8 | 59136 | 122.5 | 20435513 | 5.59 | 845.61 | 740.0597 | 1294.4747 | 1184941.99 | 589521.16 | 2139961.16 | VPC | 7.6485 | 32.2987 | 1345.2694 | 30.0065 | 20.0376 | 9.9689 | 0.94203 | 85
Madison | GA2110002 | Morgan | 6427 | 418.212 | Note 1 | 0.195 | 418.014 | 319.6708 | Note 1 | 11.908 | 0.79918 | 332.378 | 85.6361 | 10.1004 | 75.5357 | 98.3432 | 75 | 3525 | 60 | 3106491.82 | 14.88 | 640.7 | 20.4656 | 98.3432 | 145945.84 | 48395.71 | 202483.04 | VPC | 7.8503 | 58.7084 | 2759.2942 | 55.1324 | 41.4031 | 13.7293 | 3.6909 | 76
Madison County Water System | GA1950060 | Madison | 4663 | 117.2292 | 281.1194 | 16.822 | 381.5266 | 341.5691 | Note 1 | Note 1 | 0.85392 | 342.423 | 39.1036 | 6.9094 | 32.1942 | 39.9575 | 105 | 1825 | 65 | Note 2 | 5.79 | 2357.29 | 19.9717 | 39.9575 | 40005.46 | 75891.02 | 117909.42 | VPC | 10.3725 | 48.3305 | 840.0308 | 63.5049 | 21.9208 | 41.5841 | 1.612 | 63
Manchester | GA1990003 | Meriwether | 6529 | 432.347 | Note 1 | 109.983 | 333.4498 | 214.983 | Note 1 | 1.26 | 0.53746 | 216.7805 | 116.6694 | 3.2592 | 113.4102 | 118.4668 | 113 | 2359 | 66 | 2290565 | 0.65 | 590.1 | 23.2512 | 118.4668 | 34582.31 | 66923.34 | 102566.34 | VPC | 3.7852 | 131.7138 | 2749.6709 | 43.0291 | 14.6597 | 28.3694 | 4.8776 | 81
Marietta Water | GA0670005 | Cobb | 60100 | Note 1 | 2774.257 | Note 1 | 2792.4076 | 2590.979 | Note 1 | Note 1 | 6.4774 | 2597.4564 | 194.9512 | 11.9189 | 183.0323 | 201.4286 | 317.16 | 20239 | 86 | 45104230 | 7.328 | 2989.7748 | 149.1554 | 201.4286 | 87342.37 | 547225.32 | 653933.8 | VPC | 1.6134 | 24.7768 | 1581.0894 | 31.3537 | 4.3155 | 27.0382 | 1.2271 | 73
Marion County Rural Water | GA1970003 | Marion | 5705 | 340.15 | Note 1 | Note 1 | 355.9248 | 154.8224 | Note 1 | Note 1 | 0.38706 | 155.2095 | 200.7153 | 8.9227 | 191.7926 | 201.1023 | 360 | 2686 | 62 | Note 2 | 6.2784 | 555.1548 | 53.1918 | 201.1023 | 56020.43 | 106474.58 | 162709.89 | VPC | 9.1011 | 195.6289 | 1459.6088 | 60.497 | 20.8565 | 39.6406 | 3.6057 | 58
McCaysville Water Department | GA1110001 | Fannin | 7020 | 248.35 | Note 1 | Note 1 | 248.2011 | 129.592 | Note 1 | 1.14 | 0.32398 | 131.056 | 117.1451 | 1.9685 | 115.1766 | 118.6091 | 153 | 3355 | 89 | 1512861.52 | 6.12 | 1008.75 | 43.2369 | 118.6091 | 11988.27 | 116184.41 | 129649.47 | VPC | 1.6075 | 94.0544 | 2062.4338 | 38.2035 | 3.5733 | 34.6302 | 2.6639 | 69
McDonough | GA1510003 | Henry | 16187 | 396.4 | 0.679 | Note 1 | 392.2733 | 309.325 | Note 1 | Note 1 | 0.77331 | 310.0983 | 82.175 | 3.1948 | 78.9802 | 82.9483 | 90 | 5170 | 79.83 | 3680883 | 6.21 | 764.44 | 36.7837 | 82.9483 | 19839.6 | 60375.61 | 80806.37 | VPC | 1.693 | 41.8538 | 2404.2675 | 15.5155 | 3.8374 | 11.6781 | 2.1471 | 76
McRae | GA2710003 | Telfair | 7857 | 291.969 | Note 1 | Note 1 | 220.0053 | 204.05 | Note 1 | 1.731 | 0.51013 | 206.2911 | 13.7141 | 3.0988 | 10.6153 | 15.9553 | 39.8 | 2117 | 56 | 679685.04 | 2.24 | 104.16 | 10.8918 | 15.9553 | 6904.07 | 1105.69 | 8243.2 | VPC | 4.0104 | 13.7378 | 730.7292 | 3.7835 | 3.2613 | 0.52229 | 0.97461 | 67
Metter | GA0430000 | Candler | 4004 | 143.042 | Note 1 | Note 1 | 143.042 | 113.805 | Note 1 | 6.322 | 0.28451 | 120.4115 | 22.6305 | 0.56903 | 22.0615 | 29.237 | 78.5 | 2371 | 65 | 692950 | 4 | 206.43 | 18.5134 | 29.237 | 2276.1 | 4554.15 | 8194.03 | VPC | 0.65752 | 25.4924 | 769.9664 | 2.8807 | 0.95997 | 1.9208 | 1.1916 | 66
Milledgeville | GA2270000 | Baldwin | 18738 | 1669.46 | Note 1 | 50.92 | 1618.54 | 840.487 | Note 1 | 29.935 | 2.1012 | 872.5232 | 746.0168 | 12.9946 | 733.0222 | 778.053 | 225 | 9187 | 70 | 4345823.09 | 3.72 | 393.27 | 66.3099 | 778.053 | 47333.91 | 288275.64 | 348208.43 | VPC | 3.8752 | 218.6002 | 8925.689 | 36.5309 | 5.1523 | 31.3786 | 11.0545 | 65
Millen | GA1650000 | Jenkins | 4457 | 179.448 | Note 1 | Note 1 | 184.9979 | 125.671 | Note 1 | 8.819 | 1.108 | 135.598 | 49.3999 | 6.2321 | 43.1678 | 59.3269 | 50 | 2028 | 60 | Note 2 | 2.25 | 554.55 | 12.5859 | 59.3269 | 13399.23 | 23938.72 | 42842.97 | VPC | 8.4193 | 58.3176 | 2365.3607 | 18.4112 | 6.6071 | 11.8041 | 3.4298 | 45
Monroe | GA2970001 | Walton | 23997 | 1368.31 | Note 1 | 406.94 | 961.62 | 682.06 | Note 1 | Note 1 | 1.7051 | 683.7651 | 277.8548 | 5.1197 | 272.7351 | 279.56 | 243.75 | 10917 | 60 | 6661573.89 | 5.11 | 656.6 | 64.7416 | 279.56 | 26161.79 | 179077.88 | 206359.27 | VPC | 1.2848 | 68.4455 | 3065.516 | 18.8 | 2.3964 | 16.4036 | 4.2127 | 64
Montezuma | GA0930003 | Macon | 4386 | 119.405 | Note 1 | Note 1 | 119.405 | 89.841 | Note 1 | 0.395 | 0.2246 | 90.4606 | 28.9444 | 0.4492 | 28.4952 | 29.564 | 38 | 1687 | 55 | Note 2 | 4 | 519.61 | 9.207 | 29.564 | 1796.82 | 14806.39 | 16925.16 | VPC | 0.72952 | 46.2768 | 2054.4479 | 9.8419 | 1.0651 | 8.7768 | 3.0949 | 71
Monticello | GA1590000 | Jasper | 3505 | 185.5 | Note 1 | Note 1 | 189.2857 | 114.55 | Note 1 | 16.01 | 0.28637 | 130.8464 | 58.4393 | 0.57275 | 57.8666 | 74.7357 | 29.5 | 2097 | 65 | 502046.97 | 3.5 | 747.5 | 11.2491 | 74.7357 | 2004.63 | 43255.28 | 57441.44 | VPC | 0.7483 | 75.6026 | 5374.1899 | 21.5832 | 0.95595 | 20.6272 | 5.1441 | 48
Moultrie | GA0710004/GA0710021 | Colquitt | 12526 | 1369.624 | Note 1 | Note 1 | 1397.5755 | 772.523 | Note 1 | Note 1 | 152.899 | 925.422 | 472.1535 | 27.7551 | 444.3984 | 625.0525 | 210.83 | 8490 | 65 | Note 2 | 2.8 | 189.88 | 57.2743 | 625.0525 | 77714.22 | 84382.37 | 191129.06 | VPC | 8.9566 | 143.4075 | 5774.9369 | 19.0926 | 9.1536 | 9.939 | 7.7591 | 67
Nashville | GA0190002 | Berrien | 4717 | 231.346 | Note 1 | Note 1 | 259.9393 | 219.736 | Note 1 | 1.096 | 0.54934 | 221.3813 | 38.558 | 1.0987 | 37.4593 | 40.2033 | 85 | 2219 | 60 | 575000 | 1.75 | 330.08 | 17.3601 | 40.2033 | 1922.69 | 12364.57 | 14830.35 | VPC | 1.3565 | 46.2498 | 1207.391 | 6.4386 | 0.86647 | 5.5721 | 2.1578 | 50
Newnan Utilities | CS0770002 | Coweta | 52929 | 1891.01 | 30.7978 | 520.367 | 1401.8908 | 1189.585 | Note 1 | 59.257 | 2.974 | 1251.816 | 150.0748 | 5.9479 | 144.1269 | 212.3058 | 290.07 | 20666 | 85 | 11845212 | 8.32 | 593.23 | 144.8613 | 212.3058 | 49486.74 | 85500.39 | 171904.4 | VPC | 0.78853 | 19.1071 | 1361.2858 | 6.5318 | 2.3946 | 4.1372 | 0.99493 | 77
Newton County Water & Sewerage Authority | GA2170097 | Newton | 75061 | Note 1 | 4942.69 | 3057.438 | 2071.5365 | 1966.776 | Note 1 | 2.342 | 4.9169 | 1974.0349 | 97.5016 | 29.724 | 67.7776 | 104.7605 | 672 | 28241 | 100 | Note 2 | 5.78 | 2401.31 | 287.316 | 104.7605 | 171724.57 | 162755.07 | 351910.61 | VPC | 2.8836 | 6.5753 | 276.3275 | 11.8438 | 6.0807 | 5.7631 | 0.2359 | 54
North Fulton County | GA1210005 | Fulton | 263827 | Note 1 | 10089.7 | 18.13 | 10065.5107 | 9090.72 | Note 1 | 6.783 | 22.7268 | 9120.2298 | 945.2809 | 204.6692 | 740.6118 | 974.7907 | 1568 | 80293 | 98.1 | 31072656 | 4.55 | 767.91 | 734.9939 | 974.7907 | 930795.7 | 568723.19 | 1522179.77 | VPC | 6.9836 | 25.2709 | 1294.0519 | 18.6756 | 11.5925 | 7.0831 | 1.0076 | 65
Notla Water Authority | GA2910003 | Union | 17829 | 329.347 | Note 1 | Note 1 | 330.1724 | 259.47 | Note 1 | 8.381 | 33.517 | 301.368 | 28.8044 | 1.9744 | 26.8301 | 70.7024 | 549.81 | 7143 | 117.3 | 2780430 | 9.79 | 625.62 | 173.2241 | 70.7024 | 19134.76 | 16785.44 | 62132.42 | VPC | 0.75727 | 10.2908 | 133.6954 | 5.0287 | 2.6788 | 2.3499 | 0.15489 | 89
Oconee County Water Resources | GA2190000 | Oconee | 32677 | 41.198 | 1151.373 | 56.255 | 1136.316 | 976.769 | Note 1 | 16.981 | 2.466 | 996.216 | 140.1 | 4.8838 | 135.2162 | 159.547 | 354.5 | 12586 | 79.2 | 2262542.76 | 9.24 | 1753.96 | 110.0165 | 159.547 | 45126.73 | 237163.73 | 316399.72 | VPC | 1.0631 | 29.4339 | 1045.0077 | 22.4289 | 3.5855 | 18.8435 | 1.2291 | 84
Palmetto | GA1210008 | Fulton | 3900 | 111.346 | 30.1553 | Note 1 | 143.1969 | 92.688 | Note 1 | 0.251 | 0.23172 | 93.1707 | 50.0262 | 3.3378 | 46.6883 | 50.5089 | 34.5 | 1900 | 55 | Note 2 | 9.0392 | 3770.0257 | 9.4683 | 50.5089 | 30130.62 | 176016.25 | 207966.74 | VPC | 4.813 | 67.3228 | 3707.6309 | 108.4984 | 15.8582 | 92.6401 | 4.931 | 59
Paulding County Water | GA2230002 | Paulding | 117468 | 3548.6 | 1491 | 279.09 | 4764.2466 | 3428 | Note 1 | Note 1 | 8.57 | 3436.57 | 1327.6766 | 87.0992 | 1240.5774 | 1336.2466 | 1024.9 | 57713 | 95.1 | Note 2 | 0.57 | 2507.99 | 492.9609 | 1336.2466 | 920638.37 | 3111355.82 | 4053487.66 | VPC | 4.1347 | 58.8921 | 3316.2672 | 69.8628 | 15.952 | 53.9108 | 2.5166 | 63
Pelham | GA2050003 | Mitchell | 6789 | 186.068 | Note 1 | Note 1 | 153.4581 | 113.103 | Note 1 | 0.771 | 0.28276 | 114.1568 | 39.3014 | 2.8895 | 36.4119 | 40.3551 | 47 | 1507 | 56 | Note 2 | 2.65 | 425.22 | 9.8177 | 40.3551 | 7622.1 | 15483.07 | 23553.25 | VPC | 5.2531 | 66.1969 | 2122.5248 | 15.3319 | 5.0578 | 10.2741 | 3.7088 | 62
Perry | GA1530006 | Houston | 22658 | 910.353 | Note 1 | Note 1 | 901.3342 | 611.502 | Note 1 | Note 1 | 1.5288 | 613.0308 | 288.3035 | 9.2343 | 279.0692 | 289.8322 | 170.36 | 8473 | 53.6 | 2232212 | 4.31 | 407 | 42.896 | 289.8322 | 39799.82 | 113581.16 | 154003.19 | VPC | 2.9859 | 90.2364 | 4487.9851 | 18.1023 | 4.6973 | 13.4051 | 6.5057 | 74
Pickens County Water & Sewer Authority | GA2270002 | Pickens | 34024 | Note 1 | 387.4483 | 110.138 | 284.0911 | 212.7261 | Note 1 | 0.173 | 0.53182 | 213.431 | 70.6601 | 6.5226 | 64.1375 | 71.3649 | 149.3 | 3927 | 110 | Note 2 | 5.0706 | 2801.7022 | 56.08 | 71.3649 | 33063.5 | 179694.22 | 214732.4 | VPC | 4.5506 | 44.7464 | 1176.9539 | 54.1782 | 8.4195 | 45.7586 | 1.1437 | 68
Polk County Water Authority | GA2330001 | Polk | 23792 | 912.82 | 8.06 | 3.235 | 936.1794 | 597.429 | Note 1 | 14.879 | 1.4936 | 613.8016 | 322.3778 | 2.9871 | 319.3907 | 338.7504 | 440 | 9599 | 97 | 4341081.46 | 8.55 | 538.37 | 135.256 | 338.7504 | 25540.09 | 171950.35 | 206304.94 | VPC | 0.85258 | 91.1598 | 1988.7338 | 20.5741 | 2.6607 | 17.9134 | 2.3614 | 72
Pooler | GA0510001 | Chatham | 26000 | 366.543 | 710.845 | 2.195 | 1075.193 | 1007.025 | Note 1 | 1.16 | 2.5176 | 1010.7026 | 64.4904 | 7.5619 | 56.9285 | 68.168 | 119 | 12305 | 56 | 4471546 | 14.87 | 6782.49 | 50.8862 | 68.168 | 112422.01 | 386117.21 | 523482.24 | VPC | 1.6837 | 12.6752 | 1310.6604 | 40.5152 | 9.1363 | 31.3789 | 1.1187 | 65
Port Wentworth | GA0510002 | Chatham | 11746 | 2.026 | 533.894 | Note 1 | 535.92 | 26.306 | Note 1 | Note 1 | 0.065765 | 26.3718 | 509.5482 | 0.13153 | 509.4167 | 509.614 | 53.28 | 4050 | 53 | 803298 | 1.84 | 667.15 | 17.3282 | 509.614 | 242.02 | 339857.35 | 340143.25 | VPC | 0.088977 | 344.608 | 26194.8612 | 83.9752 | 0.059757 | 83.9154 | 29.3982 | 46
Quitman | GA0270002 | Brooks | 4060 | 377.229 | Note 1 | Note 1 | 377.229 | 168.134 | Note 1 | Note 1 | 0.42033 | 168.5543 | 208.6747 | 0.84067 | 207.834 | 209.095 | 50 | 2744 | 62.3 | 1227720 | 3.18 | 52.29 | 15.5106 | 209.095 | 2673.33 | 10867.64 | 13562.95 | VPC | 0.83936 | 207.5103 | 11388.1641 | 4.9348 | 0.97425 | 3.9605 | 13.3995 | 39
Reynolds Water System | GA1330046 | Greene | 12000 | 377.052 | Note 1 | Note 1 | 377.052 | 324.192 | Note 1 | Note 1 | 0.81048 | 325.0025 | 52.0495 | 4.8956 | 47.1539 | 52.86 | 228.3 | 5611 | 77 | Note 2 | 14.47 | 4788.28 | 58.3671 | 52.86 | 70839.72 | 225786.04 | 300506.57 | VPC | 2.3904 | 23.0242 | 565.8728 | 52.865 | 12.6252 | 40.2399 | 0.80788 | 65
Richmond Hill | GA0290000 | Bryan | 16068 | 691.745 | Note 1 | Note 1 | 691.745 | 566.59 | Note 1 | Note 1 | 1.4165 | 568.0065 | 123.7385 | 2.833 | 120.9056 | 125.155 | 108 | 6805 | 53 | 182850 | 3.4 | 264.33 | 31.0493 | 125.155 | 9632.03 | 31958.97 | 41965.42 | VPC | 1.1406 | 48.6772 | 3067.1125 | 6.1118 | 1.4154 | 4.6964 | 3.894 | 71
Rincon | GA1030001 | Effingham | 15654 | 356.191 | Note 1 | Note 1 | 356.191 | 316.068 | Note 1 | Note 1 | 0.79017 | 316.8582 | 39.3328 | 1.5803 | 37.7525 | 40.123 | 70 | 7395 | 53 | 233000 | 4.5 | 654.14 | 28.7844 | 40.123 | 7111.53 | 24695.41 | 32323.83 | VPC | 0.58549 | 13.9867 | 1477.5926 | 4.3011 | 0.96167 | 3.3395 | 1.3116 | 34
Ringgold | GA0470002 | Catoosa | 2743 | 116.83 | 58.0154 | Note 1 | 174.5395 | 141.022 | Note 1 | 6.56 | 0.35256 | 147.9346 | 26.6049 | 0.70511 | 25.8998 | 33.5175 | 28 | 1382 | 99.8 | 822013 | 4.27 | 2582 | 13.0693 | 33.5175 | 3010.82 | 66873.39 | 87732.42 | VPC | 1.3978 | 51.3448 | 2534.2309 | 50.5674 | 2.1786 | 48.3888 | 1.9817 | 65
Rockdale Water Resources | GA2470000 | Rockdale | 92983 | 4139.95 | Note 1 | Note 1 | 4267.9897 | 2966.718 | Note 1 | 37 | 21.308 | 3025.026 | 1242.9637 | 45.1742 | 1197.7895 | 1301.2717 | 688 | 31816 | 100 | 27569601 | 7.96 | 340.085 | 310.0485 | 1301.2717 | 356738.59 | 407350.25 | 783918.52 | VPC | 3.89 | 103.1435 | 4769.7894 | 24.0159 | 11.2126 | 12.8033 | 3.8632 | 73
Rockmart | GA2330002 | Polk | 4199 | 512.48 | Note 1 | Note 1 | 512.6851 | 365.661 | Note 1 | 5.716 | 0.91415 | 372.2912 | 140.3939 | 5.5796 | 134.8143 | 147.0241 | 67.5 | 3602 | 60 | 2018995.26 | 6.65 | 308 | 19.8299 | 147.0241 | 36738.09 | 41522.81 | 80302.99 | VPC | 4.2439 | 102.5415 | 5471.9161 | 21.7271 | 10.1994 | 11.5277 | 6.7985 | 71
Rome | GA1150002 | Floyd | 48100 | 2151 | Note 1 | 89 | 2062 | 1706 | 2.4 | 131 | 4.271 | 1843.671 | 218.329 | 8.542 | 209.787 | 353.6 | 305 | 19224 | 85 | 6729703 | 3.52 | 660 | 140.6565 | 353.6 | 30067.84 | 138459.42 | 257806.12 | VPC | 1.2174 | 29.898 | 1884.4554 | 8.7665 | 1.5641 | 7.2024 | 1.4915 | 77
Roswell | GA1210009 | Fulton | 18500 | 629.431 | 11.3 | Note 1 | 637.2089 | 507.866 | Note 1 | 10.278 | 0.502 | 518.646 | 118.5629 | 5.4583 | 113.1046 | 129.3429 | 90 | 5912 | 83.6 | 5048025 | 7.12 | 430.65 | 41.9171 | 129.3429 | 38475.98 | 48708.48 | 91826.87 | VPC | 2.5295 | 52.4147 | 3443.0612 | 14.747 | 6.5081 | 8.2389 | 2.6983 | 85
Sandersville | GA3030005 | Washington | 5654 | 678.99 | Note 1 | 96.041 | 582.949 | 396.029 | Note 1 | 12.117 | 0.99007 | 409.1361 | 173.8129 | 6.1028 | 167.7101 | 186.92 | 70.3 | 2820 | 55.3 | 1319980.08 | 3.27 | 173.34 | 16.2147 | 186.92 | 19577.25 | 29070.87 | 50920.1 | VPC | 5.9291 | 162.9361 | 6535.9846 | 17.2511 | 6.9423 | 10.3088 | 10.3431 | 57
Satilla Regional Water and Sewer Authority | GA2990001 | Ware | 10657 | 399.363 | Note 1 | Note 1 | 395.4089 | 350.978 | Note 1 | Note 1 | 0.87745 | 351.8554 | 43.5535 | 2.6345 | 40.9189 | 44.4309 | 236 | 7022 | 52 | 1922867 | 5.33 | 4814.83 | 44.2245 | 44.4309 | 14042.07 | 197017.7 | 215284.52 | VPC | 1.0279 | 15.9651 | 475.0282 | 30.0569 | 1.9997 | 28.0572 | 0.92525 | 68
Savannah - Dutch Island | GA0510027 | Chatham | 1296 | 77.3401 | Note 1 | Note 1 | 77.3401 | 66.6305 | Note 1 | Note 1 | 0.16658 | 66.7971 | 10.5431 | 1.693 | 8.8501 | 10.7096 | 8.1 | 468 | 55.76 | 160532.13 | 1.86 | 201.29 | 2.3206 | 10.7096 | 4209.47 | 1781.44 | 6024.44 | VPC | 9.9108 | 51.8095 | 2993.4354 | 12.8011 | 8.9946 | 3.8065 | 3.8137 | 54
Savannah - Georgetown Gateway | GA0510081 | Chatham | 17070 | 820.4752 | Note 1 | Note 1 | 820.6394 | 576.7548 | Note 1 | 2.4544 | 1.4419 | 580.6511 | 239.9883 | 14.7044 | 225.2839 | 243.8846 | 117 | 6972 | 55.8 | 1901919.42 | 3.78 | 200.52 | 34.1915 | 243.8846 | 74059.96 | 45173.94 | 120015.17 | VPC | 5.7782 | 88.5279 | 5275.3527 | 17.1018 | 10.6225 | 6.4793 | 6.5889 | 53
Savannah - Savannah Main | GA0510003 | Chatham | 153355 | 5052.6332 | 1441.236 | 29.3648 | 6467.5378 | 5267.679 | Note 1 | 173.8548 | 13.1692 | 5454.7029 | 1012.8349 | 194.6333 | 818.2016 | 1199.8588 | 723 | 57173 | 57.5 | 62503226.65 | 1.81 | 187.09 | 262.0789 | 1199.8588 | 458933.94 | 153077.34 | 647001.59 | VPC | 9.3268 | 39.2082 | 3100.4818 | 10.7046 | 8.0271 | 2.6774 | 3.122 | 55
Savannah - Savannah Quarters | GA0510259 | Chatham | 2798 | 108.6389 | Note 1 | 9.795 | 98.8439 | 81.1711 | Note 1 | 11.5626 | 0.20293 | 92.9367 | 5.9072 | 0.40586 | 5.5013 | 17.6728 | 26 | 1084 | 56.87 | 319812.53 | 2.97 | 201.59 | 6.2949 | 17.6728 | 1205.39 | 1109.01 | 4686.23 | VPC | 1.0258 | 13.9042 | 579.698 | 2.1351 | 1.112 | 1.0231 | 0.87393 | 62
Savannah - Whitemarsh | GA0510250 | Chatham | 4238 | 249.8541 | Note 1 | Note 1 | 249.8541 | 179.2527 | Note 1 | 0.35607 | 0.44813 | 180.0569 | 69.7972 | 4.5617 | 65.2354 | 70.6014 | 25.33 | 1708 | 59.94 | 506827.75 | 2.76 | 201.1 | 8.6032 | 70.6014 | 16805.6 | 13118.84 | 30086.17 | VPC | 7.3173 | 104.6412 | 7055.9473 | 17.5202 | 9.8393 | 7.6808 | 7.5827 | 59
Savannah - Wilmington | GA0510229 | Chatham | 13481 | 480.4664 | Note 1 | Note 1 | 480.4664 | 389.7314 | Note 1 | Note 1 | 0.97433 | 390.7057 | 89.7607 | 9.9024 | 79.8583 | 90.735 | 57.2 | 5279 | 53.55 | 1043931.09 | 2.99 | 200.6 | 21.5258 | 90.735 | 39580.21 | 16019.58 | 55795.24 | VPC | 5.1392 | 41.4453 | 3824.9995 | 10.5323 | 7.4977 | 3.0346 | 3.7099 | 57
Senoia | GA0770003 | Coweta | 5016 | 109.562 | 77.689 | Note 1 | 186.8545 | 169.397 | Note 1 | 2.135 | 0.42349 | 171.9555 | 14.899 | 0.84698 | 14.052 | 17.4575 | 70 | 2680 | 64.6 | Note 2 | 19.14 | 2088.22 | 18.4081 | 17.4575 | 16211.29 | 29343.69 | 50897.68 | VPC | 0.86586 | 14.3652 | 549.9809 | 16.9981 | 6.049 | 10.9491 | 0.76336 | 52
Smyrna Water/Sewer Division | GA0670007 | Cobb | 57000 | Note 1 | 1410.391 | Note 1 | 1343.2295 | 1301.86 | 4.625 | 19.365 | 3.2662 | 1329.1162 | 14.1133 | 6.5324 | 7.5809 | 36.7445 | 185.5 | 15279 | 113.5 | 16516653 | 5.82 | 3726 | 136.5204 | 36.7445 | 38018.71 | 28246.38 | 150588.99 | VPC | 1.1713 | 1.3594 | 111.9652 | 4.337 | 2.4883 | 1.8487 | 0.055529 | 72
Social Circle | GA2970002 | Walton | 5200 | 192.35 | 31.35 | Note 1 | 223.3827 | 142.636 | Note 1 | 8.67 | 0.35659 | 151.6626 | 71.7201 | 3.8011 | 67.919 | 80.7467 | 25.7 | 2220 | 60 | 217282.24 | 13.25 | 972.69 | 10.3376 | 80.7467 | 48191.68 | 66064.14 | 123035.9 | VPC | 4.6909 | 83.8196 | 7240.4468 | 51.4666 | 21.708 | 29.7586 | 6.5701 | 70
South Atlantic Utilities-Bryan County | GA0290080 | Bryan | 3353 | 134.3 | Note 1 | Note 1 | 134.3 | 131.4 | Note 1 | Note 1 | 0.3285 | 131.7285 | 2.5715 | 0.657 | 1.9145 | 2.9 | 12 | 1242 | 45 | Note 2 | 3.12 | 237.28 | 4.1263 | 2.9 | 2049.84 | 454.27 | 2582.06 | VPC | 1.4493 | 4.2232 | 437.1005 | 2.0162 | 1.6504 | 0.36576 | 0.46398 | 51
South Monroe County Water | GA2070074 | Monroe | 15457 | Note 1 | 315.281 | 1.495 | 333.8149 | 299.378 | Note 1 | 0.441 | 0.74845 | 300.5674 | 33.2474 | 1.4969 | 31.7506 | 34.4369 | 142.5 | 5945 | 64 | Note 2 | 8.64 | 2827 | 38.8401 | 34.4369 | 12933.13 | 89758.83 | 106054.52 | VPC | 0.68983 | 14.6321 | 610.4409 | 17.2737 | 2.1755 | 15.0982 | 0.81747 | 51
Spalding County Water/Sewerage Authority | GA2550036 | Spalding | 39000 | Note 1 | 1242.0698 | Note 1 | 1242.0698 | 864.9208 | Note 1 | 20.27 | 30.6911 | 915.8819 | 326.1879 | 13.2659 | 312.922 | 377.149 | 526 | 15863 | 102 | 9137852 | 8.71 | 6765.22 | 194.5308 | 377.149 | 115148.02 | 2116986.22 | 2576897.39 | VPC | 2.2912 | 54.0453 | 1629.887 | 140.7132 | 7.2589 | 133.4543 | 1.6086 | 77
Sparta | GA1410001 | Hancock | 3354 | 322.2 | Note 1 | 50.471 | 269.8392 | 147.6 | Note 1 | 4.2964 | 0.369 | 152.2654 | 117.5738 | 0.738 | 116.8358 | 122.2392 | 53 | 1717 | 59 | 2179633 | 15.33 | 834.99 | 11.7211 | 122.2392 | 11313.54 | 97556.7 | 112765.8 | VPC | 1.1776 | 186.4287 | 6039.5849 | 63.4072 | 6.5891 | 56.8181 | 9.968 | 72
St. Marys | GA0390001 | Camden | 18521 | 583.053 | Note 1 | Note 1 | 561.7081 | 516.741 | Note 1 | Note 1 | 1.2919 | 518.0329 | 43.6752 | 2.5837 | 41.0915 | 44.9671 | 132 | 7585 | 55.5 | Note 2 | 3.07 | 246.63 | 37.5143 | 44.9671 | 7931.97 | 10134.41 | 18384.99 | VPC | 0.93324 | 14.8424 | 852.8754 | 2.3819 | 1.0457 | 1.3361 | 1.0954 | 56
Statesboro | GA0310004 | Bulloch | 33000 | 1319.707 | Note 1 | Note 1 | 1309.31 | 1209.641 | Note 1 | Note 1 | 3.0241 | 1212.6651 | 96.6449 | 18.2668 | 78.3781 | 99.669 | 252.2 | 14842 | 62.3 | 2384477.66 | 4.47 | 292.64 | 81.6508 | 99.669 | 81652.6 | 22936.57 | 105474.14 | VPC | 3.3719 | 14.468 | 851.4453 | 7.0468 | 5.5015 | 1.5454 | 0.95992 | 64
Statham | GA0130001 | Barrow | 3986 | 41.291 | 94.9074 | Note 1 | 136.1984 | 108.8828 | Note 1 | 0.33865 | 0.502 | 109.7235 | 26.4749 | 3.9224 | 22.5525 | 27.3156 | 53 | 2083 | 83 | Note 2 | 14.5047 | 2242.0708 | 18.1522 | 27.3156 | 56764.64 | 50564.38 | 109213.83 | VPC | 5.159 | 29.6629 | 1165.807 | 51.5262 | 27.2514 | 24.2748 | 1.2424 | 63
Stockbridge | GA1510004 | Henry | 7195 | 88.8968 | 223.0008 | Note 1 | 321.4448 | 187.4758 | Note 1 | 7.3112 | 20.2 | 214.987 | 106.4578 | 4.9126 | 101.5452 | 133.969 | 49 | 2944 | 93 | 2123752.92 | 9.39 | 3272.31 | 23.9886 | 133.969 | 45216.73 | 332287.28 | 467529.27 | VPC | 4.5718 | 94.4993 | 5677.6724 | 128.2283 | 15.3589 | 112.8693 | 4.2331 | 63
Summerville | GA0550003 | Chattooga | 4500 | 874.052 | Note 1 | Note 1 | 844.4947 | 493.896 | Note 1 | Note 1 | 83.354 | 577.25 | 267.2447 | 28.464 | 238.7807 | 350.5987 | 200 | 5300 | 80 | 300042 | 5.93 | 2913 | 54.8084 | 350.5987 | 168791.56 | 695568.12 | 1107169.88 | VPC | 14.7139 | 123.4328 | 3270.9682 | 163.0867 | 31.8475 | 131.2393 | 4.3566 | 47
Swiansboro | GA1070031 | Emanuel | 7438 | 412.583 | Note 1 | Note 1 | 397.4788 | 340.839 | Note 1 | 2.02 | 0.8521 | 343.7111 | 53.7677 | 5.1674 | 48.6003 | 56.6398 | 97.2 | 3602 | 52 | Note 2 | 8.52 | 255.79 | 20.2356 | 56.6398 | 43857.77 | 12431.47 | 57023.89 | VPC | 3.9304 | 36.966 | 1369.8712 | 15.6272 | 12.1759 | 3.4513 | 2.4017 | 64
Sylvania | GA1240002 | Screven | 2660 | 244.76 | Note 1 | Note 1 | 247.7328 | 165.45 | Note 1 | Note 1 | 0.41362 | 165.8636 | 81.8692 | 9.5351 | 72.334 | 82.2828 | 60 | 1700 | 60 | 1908977 | 4.1 | 430.32 | 12.6932 | 82.2828 | 39094.09 | 31126.78 | 70398.86 | VPC | 15.3669 | 116.5738 | 3302.9235 | 41.3064 | 22.9965 | 18.3099 | 5.6986 | 54
Sylvester | CG3210003 | Worth | 7076 | 328.39 | Note 1 | Note 1 | 333.0527 | 203.316 | Note 1 | 11.063 | 0.50829 | 214.8873 | 118.1654 | 7.6469 | 110.5186 | 129.7367 | 82.3 | 3087 | 57 | 1593421 | 4.73 | 386.19 | 18.897 | 129.7367 | 34683.39 | 42681.17 | 81833.28 | VPC | 6.7866 | 98.0857 | 3679.1088 | 25.0614 | 11.2353 | 13.8261 | 5.8485 | 68
Talbot County Water Works | GA2630005 | Talbot | 3879 | Note 1 | 180.9067 | 42.9782 | 135.6422 | 80.3523 | Note 1 | 0.433 | 0.20088 | 80.9862 | 54.6561 | 4.6536 | 50.0024 | 55.2899 | 150 | 1579 | 80 | Note 2 | 4.84 | 3553.06 | 30.6118 | 55.2899 | 22494.18 | 177661.64 | 202408.04 | VPC | 8.0745 | 86.7593 | 913.2864 | 126.7611 | 14.2458 | 112.5153 | 1.6334 | 54
Tallapoosa | GA1430002 | Haralson | 4680 | Note 1 | 190.363 | Note 1 | 194.248 | 130.452 | Note 1 | Note 1 | 0.32613 | 130.7781 | 63.4698 | 0.67836 | 62.7915 | 63.796 | 31 | 1781 | 80 | Note 2 | 7.55 | 2920 | 12.6979 | 63.796 | 5121.58 | 183351.1 | 189424.99 | VPC | 1.0435 | 96.5926 | 5549.4011 | 105.8241 | 2.8757 | 102.9484 | 4.945 | 67
Temple | GA0450005 | Carroll | 2560 | Note 1 | 162.543 | Note 1 | 162.6321 | 129.161 | Note 1 | 0.42 | 0.3229 | 129.9039 | 32.7282 | 1.9547 | 30.7735 | 33.4711 | 44 | 2515 | 50 | 1444475 | 5.67 | 4147.93 | 11.229 | 33.4711 | 11076.71 | 127646.39 | 141804.61 | VPC | 2.1294 | 33.5233 | 1916.1591 | 55.1583 | 4.4043 | 50.754 | 2.7405 | 64
The Landings Subdivision - Utilities, Inc. | GA0510033 | Chatham | 12100 | 515.189 | Note 1 | Note 1 | 513.167 | 456.256 | Note 1 | 0.06 | 0.699 | 457.015 | 56.152 | 5.9999 | 50.1521 | 56.911 | 95.4 | 4726 | 58.3 | 830352 | 4.81 | 498.5 | 26.0677 | 56.911 | 28856.87 | 241231.64 | 273739.3 | CRUC | 3.4782 | 29.0739 | 1440.2834 | 57.1495 | 6.106 | 51.0435 | 1.9239 | 82
Thomaston | GA2930000 | Upson | 9889 | 706.15 | Note 1 | 54.946 | 662.3395 | 431.147 | Note 1 | 56.591 | 1.0779 | 488.8159 | 173.5236 | 17.2404 | 156.2832 | 231.1925 | 114 | 5825 | 85 | 2410614.76 | 6.42 | 679.71 | 46.2425 | 231.1925 | 100636.6 | 106227.27 | 246061.97 | VPC | 8.1088 | 73.5061 | 3755.9053 | 35.5131 | 17.2767 | 18.2364 | 3.3796 | 68
Thomasville | GA2750005 | Thomas | 18000 | 2151.518 | Note 1 | Note 1 | 2178.7524 | 1610.931 | Note 1 | 19 | 2 | 1631.931 | 546.8214 | 47.4639 | 499.3575 | 567.8214 | 275.3 | 14189 | 66.3 | 6192368 | 5.4 | 575 | 87.5471 | 567.8214 | 255379.32 | 287130.54 | 554584.85 | VPC | 9.1647 | 96.4199 | 4969.4973 | 38.2345 | 17.9984 | 20.2361 | 5.7039 | 78
Thomson-McDuffie | GA1890001 | McDuffie | 20800 | 681.89 | Note 1 | Note 1 | 695.8061 | 509.161 | Note 1 | Note 1 | 28.5 | 537.661 | 158.1451 | 12.9368 | 145.2083 | 186.6451 | 280 | 7455 | 62 | 4203243 | 0.26 | 844.58 | 59.5859 | 186.6451 | 132732.04 | 122640.01 | 279442.57 | VPC | 4.7543 | 53.3643 | 1420.8246 | 34.2551 | 17.8044 | 16.4507 | 2.437 | 74
Tifton-Tift County Water System | GA2770001 | Tift | 30940 | 1825.76 | Note 1 | Note 1 | 1825.76 | 1506.53 | Note 1 | Note 1 | 3.7663 | 1510.2963 | 315.4637 | 42.9986 | 272.4651 | 319.23 | 286.75 | 12474 | 58.7 | 3613964 | 1.43 | 298.15 | 73.327 | 319.23 | 61487.93 | 81235.48 | 143846.34 | VPC | 9.444 | 59.8429 | 2603.2425 | 11.4417 | 4.9293 | 6.5124 | 3.7158 | 64
Toccoa | GA2570001 | Stephens | 24960 | 1722.28 | Note 1 | 411.554 | 1298.8705 | 712.986 | Note 1 | 162.439 | 3.085 | 878.51 | 420.3605 | 28.7829 | 391.5776 | 585.8845 | 613.7 | 11459 | 125 | 5881383.4 | 7.03 | 515.39 | 229.9029 | 585.8845 | 171860.13 | 201815.18 | 458984.72 | VPC | 6.8817 | 93.6221 | 1748.1104 | 32.6098 | 14.9978 | 17.6119 | 1.7032 | 69
Towns County Water and Sewerage Authority | GA2810007 | Towns | 11556 | Note 1 | 275.341 | Note 1 | 275.341 | 160.095 | Note 1 | 0.024 | 3.672 | 163.791 | 111.55 | 1.2695 | 110.2805 | 115.246 | 204 | 4731 | 100 | 2350629.9 | 6.21 | 2685.45 | 66.1851 | 115.246 | 7883.19 | 296152.84 | 313961.45 | VPC | 0.73515 | 63.8635 | 1481.0707 | 64.2646 | 1.6663 | 62.5984 | 1.6662 | 65
Tybee Island | GA0510005 | Chatham | 3358 | 275.716 | Note 1 | Note 1 | 281.3429 | 238.895 | Note 1 | 6.119 | 0.59724 | 245.6112 | 35.7316 | 2.4257 | 33.3059 | 42.4479 | 33.9 | 3358 | 61.7 | 498024 | 5 | 1332.39 | 15.4738 | 42.4479 | 12015.73 | 44376.47 | 65340.85 | VPC | 1.9791 | 27.1736 | 2691.7136 | 16.7934 | 3.5782 | 13.2151 | 2.1524 | 57
Union City | GA1210010 | Fulton | 27359 | Note 1 | 558.879 | Note 1 | 575.1559 | 451.639 | Note 1 | 27.2805 | 1.1291 | 480.0486 | 95.1073 | 24.477 | 70.6303 | 123.5169 | 112 | 6294 | 82 | 2340649.76 | 11.25 | 4188.11 | 46.3921 | 123.5169 | 271434.18 | 295807.68 | 686224.38 | VPC | 10.6546 | 30.7448 | 1727.7483 | 90.1242 | 43.1259 | 46.9984 | 1.5225 | 81
Upson County Water Department | GA2930010 | Upson | 4011 | 131.705 | 31.03 | Note 1 | 162.2743 | 127.798 | Note 1 | Note 1 | 0.3195 | 128.1175 | 34.1568 | 4.5915 | 29.5653 | 34.4763 | 71.6 | 2060 | 85 | 1053880 | 9.98 | 636.3327 | 21.6044 | 34.4763 | 45823.22 | 18813.39 | 64839.92 | VPC | 6.1065 | 39.3208 | 1131.2976 | 31.377 | 22.2443 | 9.1327 | 1.3685 | 74
USAF-Moody Air Force Base | GA1850125 | Lowndes | 4770 | 124.13 | Note 1 | Note 1 | 124.13 | 6.444 | 0.7248 | 3.683 | 0.017922 | 10.8697 | 113.2603 | 0.035844 | 113.2244 | 116.9612 | 50.8 | 518 | 65 | 166119 | 2.97 | 331.26 | 8.5383 | 116.9612 | 106.46 | 37506.73 | 38839.15 | VPC | 0.18958 | 598.8493 | 6106.3766 | 72.6123 | 0.20551 | 72.4068 | 13.2608 | 63
Note A
USA-Fort Stewart Main | GA1790024 | Liberty | 27573 | 659.1 | Note 1 | Note 1 | 659.1 | 8.1 | 306 | Note 1 | 0.78525 | 314.8853 | 344.2147 | 1.5705 | 342.6442 | 345 | 161.7 | 2677 | 57 | 1084136 | 1.94 | 928 | 28.9278 | 345 | 3046.77 | 317973.86 | 321749.35 | VPC | 1.6073 | 350.6729 | 5805.5125 | 119.9181 | 1.1381 | 118.7799 | 11.8448 | 57
USAF-Robins Air Force Base Main | GA1530042 | Houston | 23967 | 549.381 | Note 1 | Note 1 | 538.6088 | 120.47 | 222.817 | 3.781 | 89.383 | 436.451 | 102.1578 | 4.9024 | 97.2555 | 195.3218 | 92 | 1668 | 65 | 579457 | 1.56 | 1075.84 | 17.7444 | 195.3218 | 7600.74 | 104631.32 | 212461.62 | VPC | 8.0522 | 159.7442 | 2896.2318 | 67.2854 | 4.5568 | 62.7286 | 5.4809 | 57
USA-Hunter Army Airfield Main | GA0510107 | Chatham | 7500 | 143.44 | 0.8 | Note 1 | 144.24 | 0.119 | 0.54 | Note 1 | 139 | 139.659 | 4.581 | 0.003295 | 4.5777 | 143.581 | 66.4 | 980 | 55 | 739836 | 67.89 | 513.05 | 11.0008 | 143.581 | 223.7 | 2348.59 | 73886.24 | VPC | 0.0092116 | 12.7976 | 188.8804 | 2.6248 | 0.22826 | 2.3965 | 0.41612 | 52
USMC-Logistics Base Albany | GA0950035 | Dougherty | 3500 | 95.1289 | Note 1 | Note 1 | 95.1289 | 20.174 | 18.974 | Note 1 | 0.09787 | 39.2459 | 55.883 | 0.39952 | 55.4835 | 55.9809 | 40.3 | 324 | 65.8 | 211051.07 | 0.32 | 2218.59 | 6.4035 | 55.9809 | 127.85 | 123095.17 | 123440.14 | VPC | 3.3783 | 469.1655 | 3771.9509 | 380.3179 | 0.39459 | 379.9233 | 8.6646 | 34
USN-Kings Bay Submarine Base | GA0390013 | Camden | 9730 | 441.196 | Note 1 | Note 1 | 441.196 | 225.01 | 178.5 | Note 1 | 1.0088 | 404.5188 | 36.6772 | 27.0187 | 9.6586 | 37.686 | 100 | 500 | 101 | 991304 | 2.17 | 2246.86 | 22.7088 | 37.686 | 58630.49 | 21701.44 | 82598.51 | VPC | 148.0475 | 52.9236 | 264.6182 | 160.6639 | 117.261 | 43.4029 | 0.42532 | 70
Utilities, Inc. (Big Canoe Subdivision) | GA2270004 | Pickens | 7522 | 194.516 | Note 1 | Note 1 | 195.1 | 102.447 | Note 1 | 2.424 | 0.2 | 105.071 | 90.029 | 2.6525 | 87.3765 | 92.653 | 94.2 | 3510 | 153.5 | Note 2 | 6.63 | 2010.61 | 58.0513 | 92.653 | 17357.29 | 175680.15 | 198313.27 | VPC | 2.0704 | 68.2016 | 2541.2716 | 54.9964 | 4.9451 | 50.0513 | 1.5052 | 76
Valdosta | GA1850002 | Lowndes | 49000 | 2666.022 | Note 1 | Note 1 | 2666.022 | 2247.547 | Note 1 | 79.04 | 5.6189 | 2332.2059 | 333.8161 | 11.2377 | 322.5784 | 418.475 | 447.347 | 22081 | 63 | 4812188 | 2.72 | 2666.02 | 131.8142 | 418.475 | 40861.65 | 860000.46 | 1126564.35 | VPC | 1.3943 | 40.0243 | 1975.5949 | 40.7981 | 1.8505 | 38.9475 | 2.4472 | 68
Vidalia | GA2790002 | Toombs | 14909 | 651.829 | Note 1 | Note 1 | 652.1551 | 436.401 | Note 1 | 37.841 | 1.091 | 475.333 | 176.8221 | 11.8604 | 164.9617 | 215.7541 | 141 | 7170 | 47 | 1413270 | 1.75 | 216.82 | 31.5362 | 215.7541 | 19571.7 | 35766.99 | 63779.93 | VPC | 4.532 | 63.0334 | 3205.3174 | 7.7181 | 2.7297 | 4.9884 | 5.2309 | 51
Vienna | GA0930004 | Dooly | 4010 | 802.8571 | Note 1 | Note 1 | 802.8414 | 574.6382 | 2 | Note 1 | 1.4416 | 578.0798 | 224.7616 | 20.6555 | 204.1061 | 226.2032 | 73 | 1505 | 55 | Note 2 | 3.83 | 197.82 | 12.4602 | 226.2032 | 79110.59 | 40376.27 | 119772.03 | VPC | 37.6016 | 371.558 | 7660.2033 | 79.3933 | 52.5652 | 26.8281 | 16.3807 | 61
Villa Rica | GA0450006 | Carroll | 18250 | 446.734 | 283.315 | Note 1 | 734.318 | 540.612 | Note 1 | 8.134 | 1.3515 | 550.0975 | 184.2205 | 6.8498 | 177.3707 | 193.706 | 139 | 7173 | 85 | 2292792 | 7.64 | 1499.92 | 56.7118 | 193.706 | 51954.72 | 266041.88 | 332224.14 | VPC | 2.6163 | 67.7467 | 3496.0228 | 44.3324 | 7.2431 | 37.0893 | 3.1276 | 70
Walker County Water and Sewer Authority | GA2950003 | Walker | 36000 | 1102.56 | 147.84 | 439 | 823.6036 | 434.173 | Note 1 | 3.7 | 1.0854 | 438.9584 | 384.6452 | 6.5938 | 378.0514 | 389.4306 | 429.4 | 13679 | 75 | 5769094.18 | 5.95 | 510.79 | 119.763 | 389.4306 | 39029.97 | 193104.85 | 234579.18 | VPC | 1.3207 | 75.7188 | 2412.1033 | 16.9702 | 2.8533 | 14.1169 | 3.1567 | 69
Walthourville | GA1790020 | Liberty | 3858 | 122.45 | Note 1 | Note 1 | 122.45 | 72.287 | Note 1 | Note 1 | 0.18072 | 72.4677 | 49.9823 | 1.0916 | 48.8907 | 50.163 | 37 | 5146 | 145.3 | 465434.8 | 7.48 | 458.54 | 51.5532 | 50.163 | 8165.22 | 22418.33 | 30666.41 | VPC | 0.58117 | 26.0294 | 3620.1907 | 5.9432 | 1.5867 | 4.3565 | 0.94835 | 49
Walton County Water Department | GA2970008 | Walton | 44460 | Note 1 | 1730 | 106 | 1640.404 | 1020 | Note 1 | Note 1 | 2.55 | 1022.55 | 617.854 | 10.2256 | 607.6284 | 620.404 | 660 | 34928 | 96 | 11500000 | 7.12 | 1400 | 343.4646 | 620.404 | 72806.47 | 850679.78 | 927056.25 | VPC | 0.80209 | 47.6619 | 2522.3263 | 26.4397 | 2.0845 | 24.3552 | 1.7691 | 78
Warner Robins | CG1530007 | Houston | 84323 | 3141.28 | 812.03 | Note 1 | 3953.31 | 2414.1 | Note 1 | Note 1 | 4.99 | 2419.09 | 1534.22 | 86.7334 | 1447.4866 | 1539.21 | 502 | 29248 | 62 | 9283846.47 | 2.39 | 538.67 | 160.7413 | 1539.21 | 207292.79 | 779717.61 | 989698.37 | VPC | 8.1245 | 135.5893 | 7899.8342 | 33.7463 | 7.0874 | 26.6588 | 9.0051 | 76
Washington | GA2450002 | Wilkes | 6490 | 362.87 | Note 1 | Note 1 | 361.7043 | 176.9368 | Note 1 | Note 1 | 0.44234 | 177.3792 | 184.3251 | 7.3021 | 177.023 | 184.7675 | 129.2 | 2976 | 80 | Note 2 | 8.8322 | 1143.598 | 33.4449 | 184.7675 | 64493.49 | 202443.2 | 267442.55 | VPC | 6.7223 | 162.9686 | 3753.8284 | 89.6965 | 21.6712 | 68.0253 | 5.293 | 63
Waycross | GA2990002 | Ware | 19900 | 794.9 | Note 1 | Note 1 | 819.4845 | 624.8 | Note 1 | 6.33 | 1.562 | 632.692 | 186.7925 | 22.6435 | 164.1491 | 194.6845 | 140 | 7609 | 50 | 677637 | 2.81 | 73.31 | 34.6522 | 194.6845 | 63092.42 | 12033.77 | 75704.75 | VPC | 8.1531 | 59.1041 | 3212.3102 | 9.8733 | 8.2918 | 1.5815 | 4.737 | 67
Waycross-Ware County Industrial Park | GA2990019 | Ware | 1700 | 217.08 | Note 1 | Note 1 | 223.7938 | 44.6 | Note 1 | Note 1 | 0.1115 | 44.7115 | 179.0823 | 1.6024 | 177.4799 | 179.1938 | 8 | 108 | 50 | 226905 | 1.22 | 94.21 | 1.0855 | 179.1938 | 1954.91 | 16720.38 | 18685.79 | VPC | 40.6489 | 4502.2814 | 60780.799 | 172.9194 | 18.101 | 154.8184 | 163.4991 | 49
Waynesboro | GA0330004 | Burke | 5600 | 296.981 | Note 1 | Note 1 | 296.981 | 191.003 | 2.762 | 36.81 | 0.48441 | 231.0594 | 65.9216 | 0.96882 | 64.9528 | 103.216 | 59 | 2457 | 46 | Note 2 | 5.4 | 732.01 | 11.5472 | 103.216 | 5231.66 | 47546.07 | 80077.61 | VPC | 1.0803 | 72.4269 | 3016.1487 | 21.4806 | 2.1293 | 19.3513 | 5.625 | 51
West Point | GA2850002 | Troup | 4308 | 514.281 | 10.112 | 0.441 | 508.9729 | 386 | Note 1 | Note 1 | 44.94 | 430.94 | 78.0329 | 9.8076 | 68.2254 | 122.9729 | 87 | 2055 | 71 | 2795810 | 3.35 | 763.17 | 20.1857 | 122.9729 | 43921.14 | 52067.57 | 130285.57 | VPC | 13.0754 | 90.9581 | 2148.4929 | 46.7098 | 21.3728 | 25.337 | 3.3799 | 75
White County Water & Sewerage Authority | GA3110072 | White | 6336 | 347.076 | 17.038 | 164.334 | 200.8249 | 160.974 | Note 1 | 6.372 | 1.044 | 168.39 | 32.4349 | 3.3533 | 29.0816 | 39.8509 | 166.9 | 2877 | 115 | Note 2 | 0.31 | 1101.57 | 56.0148 | 39.8509 | 33678.84 | 32035.38 | 73883.46 | VPC | 3.1933 | 27.694 | 477.3848 | 22.8412 | 11.7062 | 11.135 | 0.51918 | 78
Winder | GA0130002 | Barrow | 48000 | 1588.78 | 39.975 | 31.548 | 1597.207 | 1434.611 | Note 1 | 12.927 | 8.977 | 1456.515 | 140.692 | 20.2831 | 120.4089 | 162.596 | 429.45 | 18834 | 82 | Note 2 | 6.63 | 604.86 | 154.0923 | 162.596 | 133771.25 | 72830.55 | 219850.66 | VPC | 2.9505 | 17.5155 | 768.1628 | 10.9696 | 7.1026 | 3.867 | 0.78141 | 57
Woodstock Water | GA0570003 | Cherokee | 30000 | 108.344 | 680.592 | Note 1 | 788.936 | 613.037 | Note 1 | 30.252 | 1.5326 | 644.8216 | 144.1144 | 4.6774 | 139.437 | 175.899 | 105.7 | 8621 | 140.6 | Note 2 | 7.54 | 3097.76 | 95.7093 | 175.899 | 34931.07 | 431942.27 | 565334.38 | VPC | 1.4865 | 44.3126 | 3614.1825 | 54.1554 | 4.0519 | 50.1035 | 1.4569 | 74
Bowdon | GA0450000 | Carroll | 6529 | 240.51 | Note 1 | Note 1 | 246.6769 | 44.571 | Note 1 | 4.302 | 2.001 | 50.874 | 195.8029 | 0.71652 | 195.0864 | 202.1059 | 141 | 2418 | 77 | 376777 | 8.42 | 449.07 | 31.6325 | 202.1059 | 5686.74 | 87607.45 | 96124.68 | VPC | 0.81186 | 221.0435 | 3790.6616 | 38.5832 | 2.3518 | 36.2314 | 6.1673 | 81
Griffin | GA2550000 | Spalding | 120000 | 3340.976 | Note 1 | 2235.238 | 924.784 | 757.247 | Note 1 | 41.331 | 38.542 | 837.12 | 87.664 | 10.8761 | 76.7879 | 167.537 | 215.4 | 10323 | 73 | Note 2 | 9.86 | 479.94 | 72.3082 | 167.537 | 103796.53 | 36853.58 | 178984.36 | VPC | 2.8865 | 20.3795 | 976.6842 | 13.6249 | 10.0549 | 3.57 | 1.062 | 82
Hogansville | GA2850000 | Troup | 4295 | Note 1 | 157.7494 | 22.1988 | 135.5506 | 83.7996 | Note 1 | Note 1 | 0.2095 | 84.0091 | 51.5415 | 4.3677 | 47.1738 | 51.751 | 31.3 | 1920 | 100 | Note 2 | 12.62 | 3726.6952 | 16.6927 | 51.751 | 55120.01 | 175802.55 | 231703.3 | VPC | 6.2324 | 67.3143 | 4129.1827 | 120.2722 | 28.7083 | 91.5638 | 2.826 | 50
Locust Grove | GA1510002 | Henry | 11199 | 154.1312 | 120.0025 | Note 1 | 274.1338 | 244.6922 | Note 1 | 0.32435 | 0.61173 | 245.6283 | 28.5055 | 4.9547 | 23.5508 | 29.4416 | 49.5 | 4064 | 60 | 2584684 | 19.47 | 2558.3751 | 19.215 | 29.4416 | 96384.03 | 60251.86 | 159030.72 | VPC | 3.3402 | 15.8767 | 1303.4914 | 38.5423 | 23.7165 | 14.8258 | 1.2257 | 61
Louisville | GA1630002 | Jefferson | 2729 | 428.445 | Note 1 | Note 1 | 428.445 | 330.527 | Note 1 | 9.426 | 0.82632 | 340.7793 | 87.6657 | 5.0865 | 82.5792 | 97.918 | 40.5 | 1546 | 47.7 | 753856 | 2.9 | 422.41 | 7.8522 | 97.918 | 14514.96 | 34882.27 | 53727.92 | VPC | 9.014 | 146.3417 | 5586.2796 | 31.9516 | 9.3887 | 22.5629 | 10.5167 | 71
Wrightsville | GA1670002 | Johnson | 3479 | 158.102 | Note 1 | Note 1 | 166.4232 | 114.866 | Note 1 | Note 1 | 0.28717 | 115.1532 | 51.27 | 11.9347 | 39.3353 | 51.5572 | 40.1 | 898 | 60 | Note 2 | 1.87 | 790 | 7.7009 | 51.5572 | 22317.9 | 31074.88 | 53619.63 | VPC | 36.4118 | 120.0088 | 2687.4792 | 59.4574 | 24.8529 | 34.6045 | 5.1079 | 64
| Note 1 | “Note 1” represents N/A. The utility does not have uses that fit into this category.
| Note 2 | “Note 2” indicates this input has been made optional in the new V6 software, as it is no longer used in calculating a Performance Indicator.
| Note A | Moody Air force Base only consumes its water and does no billing. They also randomly meter certain buildings. Most of the older buildings have no meter in place
Yellow represents negative values (anomalies). Both the utilities and EPD are aware of these negative values (i.e. negative real losses and negative ILI values). These negative values are not credible. They are mostly due to extreme meter inaccuracies. For example, (a) over-estimation of authorized consumption, and/or (b) under-estimation of water supply, and/or (c) over-estimation of apparent losses. To resolve this issue, the utilities with negative values must (a) replace their old meters with new ones, and/or (b) perform high frequency (short intervals) recalibration and accuracy testing on a regular basis.